## gen
GEN UID | Bus ID | Gen ID | Unit Group | Unit Type | Category | Fuel | MW Inj | MVAR Inj | V Setpoint p.u. | PMax MW | PMin MW | QMax MVAR | QMin MVAR | Min Down Time Hr | Min Up Time Hr | Ramp Rate MW/Min | Start Time Cold Hr | Start Time Warm Hr | Start Time Hot Hr | Start Heat Cold MBTU | Start Heat Hot MBTU | Non Fuel Start Cost $ | Non Fuel Shutdown Cost $ | FOR | MTTF Hr | MTTR Hr | Scheduled Maint Weeks | Fuel Price $/MMBTU | Output_pct_0 | Output_pct_1 | Output_pct_2 | Output_pct_3 | Output_pct_4 | HR_avg_0 | HR_incr_1 | HR_incr_2 | HR_incr_3 | HR_incr_4 | VOM | Fuel Sulfur Content % | Emissions SO2 Lbs/MMBTU | Emissions NOX Lbs/MMBTU | Emissions Part Lbs/MMBTU | Emissions CO2 Lbs/MMBTU | Emissions CH4 Lbs/MMBTU | Emissions N2O Lbs/MMBTU | Emissions CO Lbs/MMBTU | Emissions VOCs Lbs/MMBTU | Damping Ratio | Inertia MJ/MW | Base MVA | Transformer X p.u. | Unit X p.u. | Pump Load MW | Storage Roundtrip Efficiency
101_CT_1 | 101 | 1 | U20 | CT | Oil CT | Oil | 8 | 4.96 | 1.0468 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 13114 | 9456 | 9476 | 10352 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
101_CT_2 | 101 | 2 | U20 | CT | Oil CT | Oil | 8 | 4.96 | 1.0468 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 13114 | 9456 | 9476 | 10352 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
101_STEAM_3 | 101 | 3 | U76 | STEAM | Coal | Coal | 76 | 0.14 | 1.0468 | 76 | 30 | 30 | -25 | 4 | 8 | 2 | 12 | 10 | 3 | 5284.8 | 3379.4 | 0 | 0 | 0.02 | 1960 | 40 | 3 | 2.114 | 0.39474 | 0.59649 | 0.79825 | 1 | NA | 13270 | 6713 | 8028 | 8549 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 89 | 0.13 | 0.3 | 0 | 0
101_STEAM_4 | 101 | 4 | U76 | STEAM | Coal | Coal | 76 | 0.14 | 1.0468 | 76 | 30 | 30 | -25 | 4 | 8 | 2 | 12 | 10 | 3 | 5284.8 | 3379.4 | 0 | 0 | 0.02 | 1960 | 40 | 3 | 2.114 | 0.39474 | 0.59649 | 0.79825 | 1 | NA | 13270 | 6713 | 8028 | 8549 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 89 | 0.13 | 0.3 | 0 | 0
102_CT_1 | 102 | 1 | U20 | CT | Oil CT | Oil | 8 | 4.88 | 1.0467 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 14639 | 8597 | 9147 | 9622 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
102_CT_2 | 102 | 2 | U20 | CT | Oil CT | Oil | 8 | 4.88 | 1.0467 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 14639 | 8597 | 9147 | 9622 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
102_STEAM_3 | 102 | 3 | U76 | STEAM | Coal | Coal | 76 | -2.31 | 1.0467 | 76 | 30 | 30 | -25 | 4 | 8 | 2 | 12 | 10 | 3 | 5284.8 | 3379.4 | 0 | 0 | 0.02 | 1960 | 40 | 3 | 2.114 | 0.39474 | 0.59649 | 0.79825 | 1 | NA | 11591 | 8734 | 9861 | 10651 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 89 | 0.13 | 0.3 | 0 | 0
102_STEAM_4 | 102 | 4 | U76 | STEAM | Coal | Coal | 76 | -2.31 | 1.0467 | 76 | 30 | 30 | -25 | 4 | 8 | 2 | 12 | 10 | 3 | 5284.8 | 3379.4 | 0 | 0 | 0.02 | 1960 | 40 | 3 | 2.114 | 0.39474 | 0.59649 | 0.79825 | 1 | NA | 11591 | 8734 | 9861 | 10651 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 89 | 0.13 | 0.3 | 0 | 0
107_CC_1 | 107 | 1 | U355 | CC | Gas CC | NG | 355 | 49.51 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 7222 | 5970 | 6892 | 7854 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
113_CT_1 | 113 | 1 | U55 | CT | Gas CT | NG | 55 | 19 | 1.0347 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13125 | 6899 | 7602 | 7797 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
113_CT_2 | 113 | 2 | U55 | CT | Gas CT | NG | 55 | 19 | 1.0347 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13125 | 6899 | 7602 | 7797 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
113_CT_3 | 113 | 3 | U55 | CT | Gas CT | NG | 55 | 19 | 1.0347 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13125 | 6899 | 7602 | 7797 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
113_CT_4 | 113 | 4 | U55 | CT | Gas CT | NG | 55 | 19 | 1.0347 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13125 | 6899 | 7602 | 7797 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
115_STEAM_1 | 115 | 1 | U12 | STEAM | Oil ST | Oil | 5 | 6 | 1.0428 | 12 | 5 | 6 | 0 | 2 | 4 | 1 | 12 | 4 | 2 | 68 | 38 | 0 | 0 | 0.02 | 2940 | 60 | 2 | 10.3494 | 0.41667 | 0.61111 | 0.80556 | 1 | NA | 17340 | 12030 | 12083 | 12913 | NA | 0 | Unit-Specific | Unit-specific | 0.5 | 0.1 | 170 | 0.002 | 0.004 | 0.04 | 0.007 | 0 | 2.8 | 14 | 0.13 | 0.32 | 0 | 0
115_STEAM_2 | 115 | 2 | U12 | STEAM | Oil ST | Oil | 5 | 6 | 1.0428 | 12 | 5 | 6 | 0 | 2 | 4 | 1 | 12 | 4 | 2 | 68 | 38 | 0 | 0 | 0.02 | 2940 | 60 | 2 | 10.3494 | 0.41667 | 0.61111 | 0.80556 | 1 | NA | 17340 | 12030 | 12083 | 12913 | NA | 0 | Unit-Specific | Unit-specific | 0.5 | 0.1 | 170 | 0.002 | 0.004 | 0.04 | 0.007 | 0 | 2.8 | 14 | 0.13 | 0.32 | 0 | 0
115_STEAM_3 | 115 | 3 | U155 | STEAM | Coal | Coal | 155 | 80 | 1.0428 | 155 | 62 | 80 | -50 | 8 | 8 | 3 | 60 | 11 | 3 | 10778.1 | 6892.1 | 0 | 0 | 0.04 | 960 | 40 | 4 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 11446 | 9650 | 10640 | 12796 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 182 | 0.13 | 0.3 | 0 | 0
116_STEAM_1 | 116 | 1 | U155 | STEAM | Coal | Coal | 155 | 80 | 1.0461 | 155 | 62 | 80 | -50 | 8 | 8 | 3 | 60 | 11 | 3 | 10778.1 | 6892.1 | 0 | 0 | 0.04 | 960 | 40 | 4 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 13238 | 9312 | 10158 | 11294 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 182 | 0.13 | 0.3 | 0 | 0
118_CC_1 | 118 | 1 | U355 | CC | Gas CC | NG | 355 | 68.43 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 7257 | 5808 | 7140 | 8351 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
123_STEAM_2 | 123 | 2 | U155 | STEAM | Coal | Coal | 155 | -5.19 | 1.05 | 155 | 62 | 80 | -50 | 8 | 8 | 3 | 60 | 11 | 3 | 10778.1 | 6892.1 | 0 | 0 | 0.04 | 960 | 40 | 4 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 10967 | 9191 | 10865 | 15627 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 182 | 0.13 | 0.3 | 0 | 0
123_STEAM_3 | 123 | 3 | U350 | STEAM | Coal | Coal | 350 | 28.41 | 1.05 | 350 | 140 | 150 | -25 | 48 | 24 | 4 | 96 | 12 | 8 | 17384.1 | 9768.2 | 0 | 0 | 0.08 | 1150 | 100 | 5 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 12106 | 9453 | 10240 | 11087 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 412 | 0.13 | 0.3 | 0 | 0
123_CT_1 | 123 | 1 | U55 | CT | Gas CT | NG | 55 | 0.62 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 12725 | 6757 | 7667 | 7998 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
123_CT_4 | 123 | 4 | U55 | CT | Gas CT | NG | 55 | 0.62 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 12725 | 6757 | 7667 | 7998 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
123_CT_5 | 123 | 5 | U55 | CT | Gas CT | NG | 55 | 0.62 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 12725 | 6757 | 7667 | 7998 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
201_CT_1 | 201 | 1 | U20 | CT | Oil CT | Oil | 8 | 5.29 | 1.05 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 13977 | 7969 | 8107 | 10782 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
201_CT_2 | 201 | 2 | U20 | CT | Oil CT | Oil | 8 | 5.29 | 1.05 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 13977 | 7969 | 8107 | 10782 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
201_STEAM_3 | 201 | 3 | U76 | STEAM | Coal | Coal | 76 | 6.99 | 1.05 | 76 | 30 | 30 | -25 | 4 | 8 | 2 | 12 | 10 | 3 | 5284.8 | 3379.4 | 0 | 0 | 0.02 | 1960 | 40 | 3 | 2.114 | 0.39474 | 0.59649 | 0.79825 | 1 | NA | 12989 | 10495 | 11090 | 12185 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 89 | 0.13 | 0.3 | 0 | 0
202_CT_1 | 202 | 1 | U20 | CT | Oil CT | Oil | 8 | 5.13 | 1.05 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 13663 | 7836 | 8442 | 9454 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
202_CT_2 | 202 | 2 | U20 | CT | Oil CT | Oil | 8 | 5.13 | 1.05 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 13663 | 7836 | 8442 | 9454 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
202_STEAM_3 | 202 | 3 | U76 | STEAM | Coal | Coal | 76 | 2.01 | 1.05 | 76 | 30 | 30 | -25 | 4 | 8 | 2 | 12 | 10 | 3 | 5284.8 | 3379.4 | 0 | 0 | 0.02 | 1960 | 40 | 3 | 2.114 | 0.39474 | 0.59649 | 0.79825 | 1 | NA | 11846 | 9989 | 10070 | 12902 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 89 | 0.13 | 0.3 | 0 | 0
202_STEAM_4 | 202 | 4 | U76 | STEAM | Coal | Coal | 76 | 2.01 | 1.05 | 76 | 30 | 30 | -25 | 4 | 8 | 2 | 12 | 10 | 3 | 5284.8 | 3379.4 | 0 | 0 | 0.02 | 1960 | 40 | 3 | 2.114 | 0.39474 | 0.59649 | 0.79825 | 1 | NA | 11846 | 9989 | 10070 | 12902 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 89 | 0.13 | 0.3 | 0 | 0
207_CT_1 | 207 | 1 | U55 | CT | Gas CT | NG | 55 | 19 | 0.9699 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13051 | 8804 | 9481 | 10955 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
207_CT_2 | 207 | 2 | U55 | CT | Gas CT | NG | 55 | 19 | 0.9699 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13051 | 8804 | 9481 | 10955 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
213_CC_3 | 213 | 3 | U355 | CC | Gas CC | NG | 355 | 135.8 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 7824 | 6334 | 6979 | 8749 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
213_CT_1 | 213 | 1 | U55 | CT | Gas CT | NG | 55 | 9.23 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13125 | 6899 | 7602 | 7797 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
213_CT_2 | 213 | 2 | U55 | CT | Gas CT | NG | 55 | 9.23 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13125 | 6899 | 7602 | 7797 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
215_CT_4 | 215 | 4 | U55 | CT | Gas CT | NG | 55 | 19 | 1.0437 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 14229 | 6668 | 6987 | 8421 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
215_CT_5 | 215 | 5 | U55 | CT | Gas CT | NG | 55 | 19 | 1.0437 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 14229 | 6668 | 6987 | 8421 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
216_STEAM_1 | 216 | 1 | U155 | STEAM | Coal | Coal | 155 | 80 | 1.0473 | 155 | 62 | 80 | -50 | 8 | 8 | 3 | 60 | 11 | 3 | 10778.1 | 6892.1 | 0 | 0 | 0.04 | 960 | 40 | 4 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 10881 | 8786 | 10333 | 11191 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 182 | 0.13 | 0.3 | 0 | 0
218_CC_1 | 218 | 1 | U355 | CC | Gas CC | NG | 355 | 60.3 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 11385 | 5388 | 5575 | 7658 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
221_CC_1 | 221 | 1 | U355 | CC | Gas CC | NG | 296.97 | -7.52 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 6887 | 5950 | 6772 | 9293 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
223_STEAM_1 | 223 | 1 | U155 | STEAM | Coal | Coal | 155 | -10.31 | 1.05 | 155 | 62 | 80 | -50 | 8 | 8 | 3 | 60 | 11 | 3 | 10778.1 | 6892.1 | 0 | 0 | 0.04 | 960 | 40 | 4 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 10857 | 9004 | 9314 | 9659 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 182 | 0.13 | 0.3 | 0 | 0
223_STEAM_2 | 223 | 2 | U155 | STEAM | Coal | Coal | 155 | -10.31 | 1.05 | 155 | 62 | 80 | -50 | 8 | 8 | 3 | 60 | 11 | 3 | 10778.1 | 6892.1 | 0 | 0 | 0.04 | 960 | 40 | 4 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 10857 | 9004 | 9314 | 9659 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 182 | 0.13 | 0.3 | 0 | 0
223_STEAM_3 | 223 | 3 | U350 | STEAM | Coal | Coal | 350 | 20.59 | 1.05 | 350 | 140 | 150 | -25 | 48 | 24 | 4 | 96 | 12 | 8 | 17384.1 | 9768.2 | 0 | 0 | 0.08 | 1150 | 100 | 5 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 11229 | 8922 | 10913 | 11645 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 412 | 0.13 | 0.3 | 0 | 0
223_CT_4 | 223 | 4 | U55 | CT | Gas CT | NG | 22 | 0.24 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 19794 | 9595 | 10225 | 10676 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
223_CT_5 | 223 | 5 | U55 | CT | Gas CT | NG | 22 | 0.24 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 19794 | 9595 | 10225 | 10676 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
223_CT_6 | 223 | 6 | U55 | CT | Gas CT | NG | 22 | 0.24 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 19794 | 9595 | 10225 | 10676 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
301_CT_1 | 301 | 1 | U20 | CT | Oil CT | Oil | 8 | 7.95 | 1.05 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 14593 | 8431 | 9633 | 10181 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
301_CT_2 | 301 | 2 | U20 | CT | Oil CT | Oil | 8 | 7.95 | 1.05 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 14593 | 8431 | 9633 | 10181 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
301_CT_3 | 301 | 3 | U55 | CT | Gas CT | NG | 44 | 16.53 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13090 | 7324 | 7534 | 11253 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
301_CT_4 | 301 | 4 | U55 | CT | Gas CT | NG | 44 | 16.53 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13090 | 7324 | 7534 | 11253 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
302_CT_1 | 302 | 1 | U20 | CT | Oil CT | Oil | 8 | 6.16 | 1.05 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 14593 | 8431 | 9633 | 10181 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
302_CT_2 | 302 | 2 | U20 | CT | Oil CT | Oil | 8 | 6.16 | 1.05 | 20 | 8 | 10 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 0.1 | 450 | 50 | 2 | 10.3494 | 0.4 | 0.6 | 0.8 | 1 | NA | 14593 | 8431 | 9633 | 10181 | NA | 0 | 0.2 | 0.2 | 0.5 | 0.036 | 160 | 0.002 | 0.004 | 0.11 | 0.04 | 0 | 2.8 | 24 | 0.13 | 0.32 | 0 | 0
302_CT_3 | 302 | 3 | U55 | CT | Gas CT | NG | 55 | 10.99 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 15395 | 8693 | 9874 | 9939 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
302_CT_4 | 302 | 4 | U55 | CT | Gas CT | NG | 55 | 10.99 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 15395 | 8693 | 9874 | 9939 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
307_CT_1 | 307 | 1 | U55 | CT | Gas CT | NG | 55 | 19 | 0.9568 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13353 | 7176 | 7517 | 9126 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
307_CT_2 | 307 | 2 | U55 | CT | Gas CT | NG | 55 | 19 | 0.9568 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 13353 | 7176 | 7517 | 9126 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
313_CC_1 | 313 | 1 | U355 | CC | Gas CC | NG | 355 | 150 | 1.035 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 7934 | 4047 | 6883 | 8683 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
315_STEAM_1 | 315 | 1 | U12 | STEAM | Oil ST | Oil | 5 | 6 | 1.0422 | 12 | 5 | 6 | 0 | 2 | 4 | 1 | 12 | 4 | 2 | 68 | 38 | 0 | 0 | 0.02 | 2940 | 60 | 2 | 10.3494 | 0.41667 | 0.61111 | 0.80556 | 1 | NA | 14410 | 7289 | 9701 | 11991 | NA | 0 | Unit-Specific | Unit-specific | 0.5 | 0.1 | 170 | 0.002 | 0.004 | 0.04 | 0.007 | 0 | 2.8 | 14 | 0.13 | 0.32 | 0 | 0
315_STEAM_2 | 315 | 2 | U12 | STEAM | Oil ST | Oil | 5 | 6 | 1.0422 | 12 | 5 | 6 | 0 | 2 | 4 | 1 | 12 | 4 | 2 | 68 | 38 | 0 | 0 | 0.02 | 2940 | 60 | 2 | 10.3494 | 0.41667 | 0.61111 | 0.80556 | 1 | NA | 14410 | 7289 | 9701 | 11991 | NA | 0 | Unit-Specific | Unit-specific | 0.5 | 0.1 | 170 | 0.002 | 0.004 | 0.04 | 0.007 | 0 | 2.8 | 14 | 0.13 | 0.32 | 0 | 0
315_STEAM_3 | 315 | 3 | U12 | STEAM | Oil ST | Oil | 5 | 6 | 1.0422 | 12 | 5 | 6 | 0 | 2 | 4 | 1 | 12 | 4 | 2 | 68 | 38 | 0 | 0 | 0.02 | 2940 | 60 | 2 | 10.3494 | 0.41667 | 0.61111 | 0.80556 | 1 | NA | 14410 | 7289 | 9701 | 11991 | NA | 0 | Unit-Specific | Unit-specific | 0.5 | 0.1 | 170 | 0.002 | 0.004 | 0.04 | 0.007 | 0 | 2.8 | 14 | 0.13 | 0.32 | 0 | 0
315_STEAM_4 | 315 | 4 | U12 | STEAM | Oil ST | Oil | 5 | 6 | 1.0422 | 12 | 5 | 6 | 0 | 2 | 4 | 1 | 12 | 4 | 2 | 68 | 38 | 0 | 0 | 0.02 | 2940 | 60 | 2 | 10.3494 | 0.41667 | 0.61111 | 0.80556 | 1 | NA | 14410 | 7289 | 9701 | 11991 | NA | 0 | Unit-Specific | Unit-specific | 0.5 | 0.1 | 170 | 0.002 | 0.004 | 0.04 | 0.007 | 0 | 2.8 | 14 | 0.13 | 0.32 | 0 | 0
315_STEAM_5 | 315 | 5 | U12 | STEAM | Oil ST | Oil | 5 | 6 | 1.0422 | 12 | 5 | 6 | 0 | 2 | 4 | 1 | 12 | 4 | 2 | 68 | 38 | 0 | 0 | 0.02 | 2940 | 60 | 2 | 10.3494 | 0.41667 | 0.61111 | 0.80556 | 1 | NA | 14410 | 7289 | 9701 | 11991 | NA | 0 | Unit-Specific | Unit-specific | 0.5 | 0.1 | 170 | 0.002 | 0.004 | 0.04 | 0.007 | 0 | 2.8 | 14 | 0.13 | 0.32 | 0 | 0
315_CT_6 | 315 | 6 | U55 | CT | Gas CT | NG | 55 | 19 | 1.0422 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 10342 | 6792 | 6919 | 8195 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
315_CT_7 | 315 | 7 | U55 | CT | Gas CT | NG | 55 | 19 | 1.0422 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 10342 | 6792 | 6919 | 8195 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
315_CT_8 | 315 | 8 | U55 | CT | Gas CT | NG | 55 | 60 | 1.0422 | 55 | 22 | 60 | 0 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 10342 | 6792 | 6919 | 8195 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
316_STEAM_1 | 316 | 1 | U155 | STEAM | Coal | Coal | 155 | 80 | 1.0449 | 155 | 62 | 80 | -50 | 8 | 8 | 3 | 60 | 11 | 3 | 10778.1 | 6892.1 | 0 | 0 | 0.04 | 960 | 40 | 4 | 2.114 | 0.4 | 0.6 | 0.8 | 1 | NA | 11846 | 9989 | 10070 | 12902 | NA | 0 | Unit-specific | Unit-specific | Unit-specific | Unit-specific | 210 | 0.001 | 0.004 | 0.02 | 0.003 | 0 | 3 | 182 | 0.13 | 0.3 | 0 | 0
318_CC_1 | 318 | 1 | U355 | CC | Gas CC | NG | 355 | 63.12 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 7952 | 6906 | 7017 | 8111 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
321_CC_1 | 321 | 1 | U355 | CC | Gas CC | NG | 355 | -3.34 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 7227 | 5848 | 6665 | 8733 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
322_CT_5 | 322 | 5 | U55 | CT | Gas CT | NG | 55 | -9.73 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 12064 | 6003 | 6817 | 7176 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
322_CT_6 | 322 | 6 | U55 | CT | Gas CT | NG | 55 | -9.73 | 1.05 | 55 | 22 | 19 | -15 | 2.2 | 2.2 | 3.7 | 1 | 0.75 | 0.25 | 1457.4 | 452.8 | 0 | 0 | 0.031 | 969 | 31 | 0.79 | 3.8872 | 0.4 | 0.6 | 0.8 | 1 | NA | 12064 | 6003 | 6817 | 7176 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.13 | 0.32 | 0 | 0
323_CC_1 | 323 | 1 | U355 | CC | Gas CC | NG | 355 | 37.41 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 7381 | 6799 | 7789 | 8162 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
323_CC_2 | 323 | 2 | U355 | CC | Gas CC | NG | 355 | 37.41 | 1.05 | 355 | 170 | 150 | -25 | 4.5 | 8 | 4.14 | 2 | 1 | 0.5 | 7215.1 | 3196.6 | 0 | 0 | 0.033 | 967 | 33 | 1.07 | 3.8872 | 0.47887 | 0.65258 | 0.82629 | 1 | NA | 7381 | 6799 | 7789 | 8162 | NA | 0 | 0 | 0.0006 | 0.08 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 5 | 414 | 0.13 | 0.3 | 0 | 0
114_SYNC_COND_1 | 114 | 1 | Sync_Cond | SYNC_COND | Sync_Cond | Sync_Cond | 0 | 103.32 | 1.0441 | 0 | 0 | 200 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121_NUCLEAR_1 | 121 | 1 | U400 | NUCLEAR | Nuclear | Nuclear | 400 | -21.87 | 1.05 | 400 | 396 | 200 | -50 | 48 | 24 | 20 | 9999 | 9999 | 9999 | 78978 | 9999 | 0 | 0 | 0.12 | 1100 | 150 | 6 | 0.81035 | 0.99 | 0.99333 | 0.99667 | 1 | NA | 10000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 471 | 0.15 | 0.4 | 0 | 0
122_HYDRO_1 | 122 | 1 | U50 | HYDRO | Hydro | Hydro | 50 | -6.79 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
122_HYDRO_2 | 122 | 2 | U50 | HYDRO | Hydro | Hydro | 50 | -6.79 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
122_HYDRO_3 | 122 | 3 | U50 | HYDRO | Hydro | Hydro | 50 | -6.79 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
122_HYDRO_4 | 122 | 4 | U50 | HYDRO | Hydro | Hydro | 50 | -6.79 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
122_HYDRO_5 | 122 | 5 | U50 | HYDRO | Hydro | Hydro | 50 | -6.79 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
122_HYDRO_6 | 122 | 6 | U50 | HYDRO | Hydro | Hydro | 50 | -6.79 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
201_HYDRO_4 | 201 | 4 | U50 | HYDRO | Hydro | Hydro | 50 | 4.15 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
214_SYNC_COND_1 | 214 | 1 | Sync_Cond | SYNC_COND | Sync_Cond | Sync_Cond | 0 | 125.28 | 1.05 | 0 | 0 | 200 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215_HYDRO_1 | 215 | 1 | U50 | HYDRO | Hydro | Hydro | 50 | 16 | 1.0437 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
215_HYDRO_2 | 215 | 2 | U50 | HYDRO | Hydro | Hydro | 50 | 16 | 1.0437 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
215_HYDRO_3 | 215 | 3 | U50 | HYDRO | Hydro | Hydro | 50 | 16 | 1.0437 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
222_HYDRO_1 | 222 | 1 | U50 | HYDRO | Hydro | Hydro | 50 | -6.97 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
222_HYDRO_2 | 222 | 2 | U50 | HYDRO | Hydro | Hydro | 50 | -6.97 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
222_HYDRO_3 | 222 | 3 | U50 | HYDRO | Hydro | Hydro | 50 | -6.97 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
222_HYDRO_4 | 222 | 4 | U50 | HYDRO | Hydro | Hydro | 50 | -6.97 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
222_HYDRO_5 | 222 | 5 | U50 | HYDRO | Hydro | Hydro | 50 | -6.97 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
222_HYDRO_6 | 222 | 6 | U50 | HYDRO | Hydro | Hydro | 50 | -6.97 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
314_SYNC_COND_1 | 314 | 1 | Sync_Cond | SYNC_COND | Sync_Cond | Sync_Cond | 0 | 166.63 | 1.05 | 0 | 0 | 200 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322_HYDRO_1 | 322 | 1 | U50 | HYDRO | Hydro | Hydro | 50 | -5.13 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
322_HYDRO_2 | 322 | 2 | U50 | HYDRO | Hydro | Hydro | 50 | -5.13 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
322_HYDRO_3 | 322 | 3 | U50 | HYDRO | Hydro | Hydro | 50 | -5.13 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
322_HYDRO_4 | 322 | 4 | U50 | HYDRO | Hydro | Hydro | 50 | -5.13 | 1.05 | 50 | 0 | 16 | -10 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 1980 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | NA | 3412 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 53 | 0.1 | 0.28 | 0 | 0
320_PV_1 | 320 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 51.6 | 0 | 0 | 0 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314_PV_1 | 314 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 51.6 | 0 | 0 | 0 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314_PV_2 | 314 | 2 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 51.6 | 0 | 0 | 0 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_PV_1 | 313 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 95.1 | 0 | 0 | 0 | 0 | 0 | 95.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314_PV_3 | 314 | 3 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 92.7 | 0 | 0 | 0 | 0 | 0 | 92.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314_PV_4 | 314 | 4 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 51.6 | 0 | 0 | 0 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_PV_2 | 313 | 2 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 93.3 | 0 | 0 | 0 | 0 | 0 | 93.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310_PV_1 | 310 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 51.7 | 0 | 0 | 0 | 0 | 0 | 51.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324_PV_1 | 324 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 49.7 | 0 | 0 | 0 | 0 | 0 | 49.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312_PV_1 | 312 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 94.1 | 0 | 0 | 0 | 0 | 0 | 94.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310_PV_2 | 310 | 2 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 51.6 | 0 | 0 | 0 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324_PV_2 | 324 | 2 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 51.6 | 0 | 0 | 0 | 0 | 0 | 51.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324_PV_3 | 324 | 3 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 51 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113_PV_1 | 113 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 93.6 | 0 | 0 | 0 | 0 | 0 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319_PV_1 | 319 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 188.2 | 0 | 0 | 0 | 0 | 0 | 188.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215_PV_1 | 215 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 125.1 | 0 | 0 | 0 | 0 | 0 | 125.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102_PV_1 | 102 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 25.6 | 0 | 0 | 0 | 0 | 0 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101_PV_1 | 101 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 25.9 | 0 | 0 | 0 | 0 | 0 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102_PV_2 | 102 | 2 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 25.3 | 0 | 0 | 0 | 0 | 0 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104_PV_1 | 104 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 26.8 | 0 | 0 | 0 | 0 | 0 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212_CSP_1 | 212 | 1 | CSP | CSP | CSP | Solar | 0 | 0 | 1 | 200 | 30 | 0 | 0 | 1 | 1 | 20 | 1 | 0.5 | 0.17 | 0 | 0 | 10000 | 10000 | 0.04 | 576 | 24 | 0 | 0 | 0.15 | 0.33 | 0.6 | 0.8 | 1 | 0.83 | 0.98948 | 1.055 | 1.0553 | 1.0421 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101_PV_2 | 101 | 2 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 26.7 | 0 | 0 | 0 | 0 | 0 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101_PV_3 | 101 | 3 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 26.2 | 0 | 0 | 0 | 0 | 0 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101_PV_4 | 101 | 4 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 25.8 | 0 | 0 | 0 | 0 | 0 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103_PV_1 | 103 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 61.5 | 0 | 0 | 0 | 0 | 0 | 61.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119_PV_1 | 119 | 1 | PV | PV | Solar PV | Solar | 0 | 0 | 1 | 66.6 | 0 | 0 | 0 | 0 | 0 | 66.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308_RTPV_1 | 308 | 1 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 100.9 | 0 | 0 | 0 | 0 | 0 | 100.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_1 | 313 | 1 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 101.7 | 0 | 0 | 0 | 0 | 0 | 101.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_2 | 313 | 2 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 63.1 | 0 | 0 | 0 | 0 | 0 | 63.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_3 | 313 | 3 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 65.4 | 0 | 0 | 0 | 0 | 0 | 65.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_4 | 313 | 4 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 67 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_5 | 313 | 5 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 64.8 | 0 | 0 | 0 | 0 | 0 | 64.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_6 | 313 | 6 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 63.8 | 0 | 0 | 0 | 0 | 0 | 63.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_7 | 313 | 7 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 64.1 | 0 | 0 | 0 | 0 | 0 | 64.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_8 | 313 | 8 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 66.6 | 0 | 0 | 0 | 0 | 0 | 66.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_9 | 313 | 9 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 62.4 | 0 | 0 | 0 | 0 | 0 | 62.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_10 | 313 | 10 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 66.9 | 0 | 0 | 0 | 0 | 0 | 66.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_11 | 313 | 11 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 65.2 | 0 | 0 | 0 | 0 | 0 | 65.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_12 | 313 | 12 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 27.8 | 0 | 0 | 0 | 0 | 0 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320_RTPV_1 | 320 | 1 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 27.3 | 0 | 0 | 0 | 0 | 0 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320_RTPV_2 | 320 | 2 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320_RTPV_3 | 320 | 3 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 28.3 | 0 | 0 | 0 | 0 | 0 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_RTPV_13 | 313 | 13 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 27.2 | 0 | 0 | 0 | 0 | 0 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320_RTPV_4 | 320 | 4 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320_RTPV_5 | 320 | 5 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 28.2 | 0 | 0 | 0 | 0 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_1 | 118 | 1 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 9.3 | 0 | 0 | 0 | 0 | 0 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_2 | 118 | 2 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_3 | 118 | 3 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 9.4 | 0 | 0 | 0 | 0 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_4 | 118 | 4 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 9.1 | 0 | 0 | 0 | 0 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_5 | 118 | 5 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 9.1 | 0 | 0 | 0 | 0 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_6 | 118 | 6 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320_RTPV_6 | 320 | 6 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 9.4 | 0 | 0 | 0 | 0 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_7 | 118 | 7 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 11.8 | 0 | 0 | 0 | 0 | 0 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_8 | 118 | 8 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 11.2 | 0 | 0 | 0 | 0 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_9 | 118 | 9 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 10.3 | 0 | 0 | 0 | 0 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118_RTPV_10 | 118 | 10 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 4.5 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213_RTPV_1 | 213 | 1 | RTPV | RTPV | Solar RTPV | Solar | 0 | 0 | 1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309_WIND_1 | 309 | 1 | WIND | WIND | Wind | Wind | 0 | 0 | 1 | 148.3 | 0 | 0 | 0 | 0 | 0 | 148.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317_WIND_1 | 317 | 1 | WIND | WIND | Wind | Wind | 0 | 0 | 1 | 799.1 | 0 | 0 | 0 | 0 | 0 | 799.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303_WIND_1 | 303 | 1 | WIND | WIND | Wind | Wind | 0 | 0 | 1 | 847 | 0 | 0 | 0 | 0 | 0 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122_WIND_1 | 122 | 1 | WIND | WIND | Wind | Wind | 0 | 0 | 1 | 713.5 | 0 | 0 | 0 | 0 | 0 | 713.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313_STORAGE_1 | 313 | 1 | STORAGE | STORAGE | Storage | Storage | 0 | 0 | 1 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 85

## Spine
GEN UID | Region (Node) | commodity | para_name_1 | value [MW] | para_name_2 | value [$/MWh] | para_name_3 | value [$/MW] | para_name_4 | rate | para_name_5 | value [$] | para_name_6 | value [$]
101_CT_1 | 1 | electricity | unit_capacity | 20 | fuel_cost | 114.9032 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
101_CT_2 | 1 | electricity | unit_capacity | 20 | fuel_cost | 114.9032 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
101_STEAM_3 | 1 | electricity | unit_capacity | 76 | fuel_cost | 21.0068 | vom_cost | 0 | minimum_operating_point | 0.39474 | start_up_cost | 11.172 | shut_down_cost | 0
101_STEAM_4 | 1 | electricity | unit_capacity | 76 | fuel_cost | 21.0068 | vom_cost | 0 | minimum_operating_point | 0.39474 | start_up_cost | 11.172 | shut_down_cost | 0
102_CT_1 | 1 | electricity | unit_capacity | 20 | fuel_cost | 117.2463 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
102_CT_2 | 1 | electricity | unit_capacity | 20 | fuel_cost | 117.2463 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
102_STEAM_3 | 1 | electricity | unit_capacity | 76 | fuel_cost | 22.146 | vom_cost | 0 | minimum_operating_point | 0.39474 | start_up_cost | 11.172 | shut_down_cost | 0
102_STEAM_4 | 1 | electricity | unit_capacity | 76 | fuel_cost | 22.146 | vom_cost | 0 | minimum_operating_point | 0.39474 | start_up_cost | 11.172 | shut_down_cost | 0
107_CC_1 | 1 | electricity | unit_capacity | 355 | fuel_cost | 27.432 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
113_CT_1 | 1 | electricity | unit_capacity | 55 | fuel_cost | 37.7434 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
113_CT_2 | 1 | electricity | unit_capacity | 55 | fuel_cost | 37.7434 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
113_CT_3 | 1 | electricity | unit_capacity | 55 | fuel_cost | 37.7434 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
113_CT_4 | 1 | electricity | unit_capacity | 55 | fuel_cost | 37.7434 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
115_STEAM_1 | 1 | electricity | unit_capacity | 12 | fuel_cost | 149.2849 | vom_cost | 0 | minimum_operating_point | 0.41667 | start_up_cost | 0.70376 | shut_down_cost | 0
115_STEAM_2 | 1 | electricity | unit_capacity | 12 | fuel_cost | 149.2849 | vom_cost | 0 | minimum_operating_point | 0.41667 | start_up_cost | 0.70376 | shut_down_cost | 0
115_STEAM_3 | 1 | electricity | unit_capacity | 155 | fuel_cost | 23.6674 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 22.7848 | shut_down_cost | 0
116_STEAM_1 | 1 | electricity | unit_capacity | 155 | fuel_cost | 24.201 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 22.7848 | shut_down_cost | 0
118_CC_1 | 1 | electricity | unit_capacity | 355 | fuel_cost | 27.8908 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
123_STEAM_2 | 1 | electricity | unit_capacity | 155 | fuel_cost | 24.3604 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 22.7848 | shut_down_cost | 0
123_STEAM_3 | 1 | electricity | unit_capacity | 350 | fuel_cost | 23.2505 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 36.7498 | shut_down_cost | 0
123_CT_1 | 1 | electricity | unit_capacity | 55 | fuel_cost | 37.2178 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
123_CT_4 | 1 | electricity | unit_capacity | 55 | fuel_cost | 37.2178 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
123_CT_5 | 1 | electricity | unit_capacity | 55 | fuel_cost | 37.2178 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
201_CT_1 | 2 | electricity | unit_capacity | 20 | fuel_cost | 113.4543 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
201_CT_2 | 2 | electricity | unit_capacity | 20 | fuel_cost | 113.4543 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
201_STEAM_3 | 2 | electricity | unit_capacity | 76 | fuel_cost | 25.2421 | vom_cost | 0 | minimum_operating_point | 0.39474 | start_up_cost | 11.172 | shut_down_cost | 0
202_CT_1 | 2 | electricity | unit_capacity | 20 | fuel_cost | 109.8237 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
202_CT_2 | 2 | electricity | unit_capacity | 20 | fuel_cost | 109.8237 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
202_STEAM_3 | 2 | electricity | unit_capacity | 76 | fuel_cost | 23.9432 | vom_cost | 0 | minimum_operating_point | 0.39474 | start_up_cost | 11.172 | shut_down_cost | 0
202_STEAM_4 | 2 | electricity | unit_capacity | 76 | fuel_cost | 23.9432 | vom_cost | 0 | minimum_operating_point | 0.39474 | start_up_cost | 11.172 | shut_down_cost | 0
207_CT_1 | 2 | electricity | unit_capacity | 55 | fuel_cost | 43.0253 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
207_CT_2 | 2 | electricity | unit_capacity | 55 | fuel_cost | 43.0253 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
213_CC_3 | 2 | electricity | unit_capacity | 355 | fuel_cost | 29.4615 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
213_CT_1 | 2 | electricity | unit_capacity | 55 | fuel_cost | 37.7434 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
213_CT_2 | 2 | electricity | unit_capacity | 55 | fuel_cost | 37.7434 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
215_CT_4 | 2 | electricity | unit_capacity | 55 | fuel_cost | 39.2874 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
215_CT_5 | 2 | electricity | unit_capacity | 55 | fuel_cost | 39.2874 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
216_STEAM_1 | 2 | electricity | unit_capacity | 155 | fuel_cost | 22.0159 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 22.7848 | shut_down_cost | 0
218_CC_1 | 2 | electricity | unit_capacity | 355 | fuel_cost | 33.7667 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
221_CC_1 | 2 | electricity | unit_capacity | 355 | fuel_cost | 27.6856 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
223_STEAM_1 | 2 | electricity | unit_capacity | 155 | fuel_cost | 21.0093 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 22.7848 | shut_down_cost | 0
223_STEAM_2 | 2 | electricity | unit_capacity | 155 | fuel_cost | 21.0093 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 22.7848 | shut_down_cost | 0
223_STEAM_3 | 2 | electricity | unit_capacity | 350 | fuel_cost | 22.8049 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 36.7498 | shut_down_cost | 0
223_CT_4 | 2 | electricity | unit_capacity | 55 | fuel_cost | 54.4864 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
223_CT_5 | 2 | electricity | unit_capacity | 55 | fuel_cost | 54.4864 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
223_CT_6 | 2 | electricity | unit_capacity | 55 | fuel_cost | 54.4864 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
301_CT_1 | 3 | electricity | unit_capacity | 20 | fuel_cost | 118.8753 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
301_CT_2 | 3 | electricity | unit_capacity | 20 | fuel_cost | 118.8753 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
301_CT_3 | 3 | electricity | unit_capacity | 55 | fuel_cost | 40.6533 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
301_CT_4 | 3 | electricity | unit_capacity | 55 | fuel_cost | 40.6533 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
302_CT_1 | 3 | electricity | unit_capacity | 20 | fuel_cost | 118.8753 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
302_CT_2 | 3 | electricity | unit_capacity | 20 | fuel_cost | 118.8753 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 0.051747 | shut_down_cost | 0
302_CT_3 | 3 | electricity | unit_capacity | 55 | fuel_cost | 46.0993 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
302_CT_4 | 3 | electricity | unit_capacity | 55 | fuel_cost | 46.0993 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
307_CT_1 | 3 | electricity | unit_capacity | 55 | fuel_cost | 39.2804 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
307_CT_2 | 3 | electricity | unit_capacity | 55 | fuel_cost | 39.2804 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
313_CC_1 | 3 | electricity | unit_capacity | 355 | fuel_cost | 28.0126 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
315_STEAM_1 | 3 | electricity | unit_capacity | 12 | fuel_cost | 120.4604 | vom_cost | 0 | minimum_operating_point | 0.41667 | start_up_cost | 0.70376 | shut_down_cost | 0
315_STEAM_2 | 3 | electricity | unit_capacity | 12 | fuel_cost | 120.4604 | vom_cost | 0 | minimum_operating_point | 0.41667 | start_up_cost | 0.70376 | shut_down_cost | 0
315_STEAM_3 | 3 | electricity | unit_capacity | 12 | fuel_cost | 120.4604 | vom_cost | 0 | minimum_operating_point | 0.41667 | start_up_cost | 0.70376 | shut_down_cost | 0
315_STEAM_4 | 3 | electricity | unit_capacity | 12 | fuel_cost | 120.4604 | vom_cost | 0 | minimum_operating_point | 0.41667 | start_up_cost | 0.70376 | shut_down_cost | 0
315_STEAM_5 | 3 | electricity | unit_capacity | 12 | fuel_cost | 120.4604 | vom_cost | 0 | minimum_operating_point | 0.41667 | start_up_cost | 0.70376 | shut_down_cost | 0
315_CT_6 | 3 | electricity | unit_capacity | 55 | fuel_cost | 33.1113 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
315_CT_7 | 3 | electricity | unit_capacity | 55 | fuel_cost | 33.1113 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
315_CT_8 | 3 | electricity | unit_capacity | 55 | fuel_cost | 33.1113 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
316_STEAM_1 | 3 | electricity | unit_capacity | 155 | fuel_cost | 23.9528 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 22.7848 | shut_down_cost | 0
318_CC_1 | 3 | electricity | unit_capacity | 355 | fuel_cost | 29.6809 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
321_CC_1 | 3 | electricity | unit_capacity | 355 | fuel_cost | 27.7992 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
322_CT_5 | 3 | electricity | unit_capacity | 55 | fuel_cost | 34.3039 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
322_CT_6 | 3 | electricity | unit_capacity | 55 | fuel_cost | 34.3039 | vom_cost | 0 | minimum_operating_point | 0.4 | start_up_cost | 5.6652 | shut_down_cost | 0
323_CC_1 | 3 | electricity | unit_capacity | 355 | fuel_cost | 29.1014 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
323_CC_2 | 3 | electricity | unit_capacity | 355 | fuel_cost | 29.1014 | vom_cost | 0 | minimum_operating_point | 0.47887 | start_up_cost | 28.0467 | shut_down_cost | 0
114_SYNC_COND_1 | 1 | electricity | unit_capacity | 0 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
121_NUCLEAR_1 | 1 | electricity | unit_capacity | 400 | fuel_cost | 8.0225 | vom_cost | 0 | minimum_operating_point | 0.99 | start_up_cost | 63.9998 | shut_down_cost | 0
122_HYDRO_1 | 1 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
122_HYDRO_2 | 1 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
122_HYDRO_3 | 1 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
122_HYDRO_4 | 1 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
122_HYDRO_5 | 1 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
122_HYDRO_6 | 1 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
201_HYDRO_4 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
214_SYNC_COND_1 | 2 | electricity | unit_capacity | 0 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
215_HYDRO_1 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
215_HYDRO_2 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
215_HYDRO_3 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
222_HYDRO_1 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
222_HYDRO_2 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
222_HYDRO_3 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
222_HYDRO_4 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
222_HYDRO_5 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
222_HYDRO_6 | 2 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
314_SYNC_COND_1 | 3 | electricity | unit_capacity | 0 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
322_HYDRO_1 | 3 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
322_HYDRO_2 | 3 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
322_HYDRO_3 | 3 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
322_HYDRO_4 | 3 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
320_PV_1 | 3 | electricity | unit_capacity | 51.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
314_PV_1 | 3 | electricity | unit_capacity | 51.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
314_PV_2 | 3 | electricity | unit_capacity | 51.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_PV_1 | 3 | electricity | unit_capacity | 95.1 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
314_PV_3 | 3 | electricity | unit_capacity | 92.7 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
314_PV_4 | 3 | electricity | unit_capacity | 51.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_PV_2 | 3 | electricity | unit_capacity | 93.3 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
310_PV_1 | 3 | electricity | unit_capacity | 51.7 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
324_PV_1 | 3 | electricity | unit_capacity | 49.7 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
312_PV_1 | 3 | electricity | unit_capacity | 94.1 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
310_PV_2 | 3 | electricity | unit_capacity | 51.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
324_PV_2 | 3 | electricity | unit_capacity | 51.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
324_PV_3 | 3 | electricity | unit_capacity | 51 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
113_PV_1 | 1 | electricity | unit_capacity | 93.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
319_PV_1 | 3 | electricity | unit_capacity | 188.2 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
215_PV_1 | 2 | electricity | unit_capacity | 125.1 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
102_PV_1 | 1 | electricity | unit_capacity | 25.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
101_PV_1 | 1 | electricity | unit_capacity | 25.9 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
102_PV_2 | 1 | electricity | unit_capacity | 25.3 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
104_PV_1 | 1 | electricity | unit_capacity | 26.8 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
212_CSP_1 | 2 | electricity | unit_capacity | 200 | fuel_cost | 0 | vom_cost | 1100 | minimum_operating_point | 0.15 | start_up_cost | 10000 | shut_down_cost | 10000
101_PV_2 | 1 | electricity | unit_capacity | 26.7 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
101_PV_3 | 1 | electricity | unit_capacity | 26.2 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
101_PV_4 | 1 | electricity | unit_capacity | 25.8 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
103_PV_1 | 1 | electricity | unit_capacity | 61.5 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
119_PV_1 | 1 | electricity | unit_capacity | 66.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
308_RTPV_1 | 3 | electricity | unit_capacity | 100.9 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_1 | 3 | electricity | unit_capacity | 101.7 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_2 | 3 | electricity | unit_capacity | 63.1 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_3 | 3 | electricity | unit_capacity | 65.4 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_4 | 3 | electricity | unit_capacity | 67 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_5 | 3 | electricity | unit_capacity | 64.8 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_6 | 3 | electricity | unit_capacity | 63.8 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_7 | 3 | electricity | unit_capacity | 64.1 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_8 | 3 | electricity | unit_capacity | 66.6 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_9 | 3 | electricity | unit_capacity | 62.4 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_10 | 3 | electricity | unit_capacity | 66.9 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_11 | 3 | electricity | unit_capacity | 65.2 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_12 | 3 | electricity | unit_capacity | 27.8 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
320_RTPV_1 | 3 | electricity | unit_capacity | 27.3 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
320_RTPV_2 | 3 | electricity | unit_capacity | 27 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
320_RTPV_3 | 3 | electricity | unit_capacity | 28.3 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_RTPV_13 | 3 | electricity | unit_capacity | 27.2 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
320_RTPV_4 | 3 | electricity | unit_capacity | 27 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
320_RTPV_5 | 3 | electricity | unit_capacity | 28.2 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_1 | 1 | electricity | unit_capacity | 9.3 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_2 | 1 | electricity | unit_capacity | 9.7 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_3 | 1 | electricity | unit_capacity | 9.4 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_4 | 1 | electricity | unit_capacity | 9.1 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_5 | 1 | electricity | unit_capacity | 9.1 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_6 | 1 | electricity | unit_capacity | 9.7 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
320_RTPV_6 | 3 | electricity | unit_capacity | 9.4 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_7 | 1 | electricity | unit_capacity | 11.8 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_8 | 1 | electricity | unit_capacity | 11.2 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_9 | 1 | electricity | unit_capacity | 10.3 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
118_RTPV_10 | 1 | electricity | unit_capacity | 4.5 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
213_RTPV_1 | 2 | electricity | unit_capacity | 13.2 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
309_WIND_1 | 3 | electricity | unit_capacity | 148.3 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
317_WIND_1 | 3 | electricity | unit_capacity | 799.1 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
303_WIND_1 | 3 | electricity | unit_capacity | 847 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
122_WIND_1 | 1 | electricity | unit_capacity | 713.5 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0
313_STORAGE_1 | 3 | electricity | unit_capacity | 50 | fuel_cost | 0 | vom_cost | 0 | minimum_operating_point | 0 | start_up_cost | 0 | shut_down_cost | 0

## obj_unit
parameter_name
obj_class name | obj_name | min_down_time | min_up_time | start_up_cost | shut_down_cost | number_of_units | unit_availability_factor | min_down_time | duration | rounded | duration | min_up_time | duration | rounded | duration
unit | 101_CT_1 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 101_CT_2 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 101_STEAM_3 | 240m | 480m | 11.172 | 0 | 1 | 1 | 4 | 240m | 4 | 4h | 8 | 480m | 8 | 8h
unit | 101_STEAM_4 | 240m | 480m | 11.172 | 0 | 1 | 1 | 4 | 240m | 4 | 4h | 8 | 480m | 8 | 8h
unit | 102_CT_1 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 102_CT_2 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 102_STEAM_3 | 240m | 480m | 11.172 | 0 | 1 | 1 | 4 | 240m | 4 | 4h | 8 | 480m | 8 | 8h
unit | 102_STEAM_4 | 240m | 480m | 11.172 | 0 | 1 | 1 | 4 | 240m | 4 | 4h | 8 | 480m | 8 | 8h
unit | 107_CC_1 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 113_CT_1 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 113_CT_2 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 113_CT_3 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 113_CT_4 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 115_STEAM_1 | 120m | 240m | 0.70376 | 0 | 1 | 1 | 2 | 120m | 2 | 2h | 4 | 240m | 4 | 4h
unit | 115_STEAM_2 | 120m | 240m | 0.70376 | 0 | 1 | 1 | 2 | 120m | 2 | 2h | 4 | 240m | 4 | 4h
unit | 115_STEAM_3 | 480m | 480m | 22.7848 | 0 | 1 | 1 | 8 | 480m | 8 | 8h | 8 | 480m | 8 | 8h
unit | 116_STEAM_1 | 480m | 480m | 22.7848 | 0 | 1 | 1 | 8 | 480m | 8 | 8h | 8 | 480m | 8 | 8h
unit | 118_CC_1 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 123_STEAM_2 | 480m | 480m | 22.7848 | 0 | 1 | 1 | 8 | 480m | 8 | 8h | 8 | 480m | 8 | 8h
unit | 123_STEAM_3 | 2880m | 1440m | 36.7498 | 0 | 1 | 1 | 48 | 2880m | 48 | 48h | 24 | 1440m | 24 | 24h
unit | 123_CT_1 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 123_CT_4 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 123_CT_5 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 201_CT_1 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 201_CT_2 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 201_STEAM_3 | 240m | 480m | 11.172 | 0 | 1 | 1 | 4 | 240m | 4 | 4h | 8 | 480m | 8 | 8h
unit | 202_CT_1 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 202_CT_2 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 202_STEAM_3 | 240m | 480m | 11.172 | 0 | 1 | 1 | 4 | 240m | 4 | 4h | 8 | 480m | 8 | 8h
unit | 202_STEAM_4 | 240m | 480m | 11.172 | 0 | 1 | 1 | 4 | 240m | 4 | 4h | 8 | 480m | 8 | 8h
unit | 207_CT_1 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 207_CT_2 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 213_CC_3 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 213_CT_1 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 213_CT_2 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 215_CT_4 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 215_CT_5 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 216_STEAM_1 | 480m | 480m | 22.7848 | 0 | 1 | 1 | 8 | 480m | 8 | 8h | 8 | 480m | 8 | 8h
unit | 218_CC_1 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 221_CC_1 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 223_STEAM_1 | 480m | 480m | 22.7848 | 0 | 1 | 1 | 8 | 480m | 8 | 8h | 8 | 480m | 8 | 8h
unit | 223_STEAM_2 | 480m | 480m | 22.7848 | 0 | 1 | 1 | 8 | 480m | 8 | 8h | 8 | 480m | 8 | 8h
unit | 223_STEAM_3 | 2880m | 1440m | 36.7498 | 0 | 1 | 1 | 48 | 2880m | 48 | 48h | 24 | 1440m | 24 | 24h
unit | 223_CT_4 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 223_CT_5 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 223_CT_6 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 301_CT_1 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 301_CT_2 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 301_CT_3 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 301_CT_4 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 302_CT_1 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 302_CT_2 | 60m | 60m | 0.051747 | 0 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 302_CT_3 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 302_CT_4 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 307_CT_1 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 307_CT_2 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 313_CC_1 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 315_STEAM_1 | 120m | 240m | 0.70376 | 0 | 1 | 1 | 2 | 120m | 2 | 2h | 4 | 240m | 4 | 4h
unit | 315_STEAM_2 | 120m | 240m | 0.70376 | 0 | 1 | 1 | 2 | 120m | 2 | 2h | 4 | 240m | 4 | 4h
unit | 315_STEAM_3 | 120m | 240m | 0.70376 | 0 | 1 | 1 | 2 | 120m | 2 | 2h | 4 | 240m | 4 | 4h
unit | 315_STEAM_4 | 120m | 240m | 0.70376 | 0 | 1 | 1 | 2 | 120m | 2 | 2h | 4 | 240m | 4 | 4h
unit | 315_STEAM_5 | 120m | 240m | 0.70376 | 0 | 1 | 1 | 2 | 120m | 2 | 2h | 4 | 240m | 4 | 4h
unit | 315_CT_6 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 315_CT_7 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 315_CT_8 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 316_STEAM_1 | 480m | 480m | 22.7848 | 0 | 1 | 1 | 8 | 480m | 8 | 8h | 8 | 480m | 8 | 8h
unit | 318_CC_1 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 321_CC_1 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 322_CT_5 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 322_CT_6 | 132m | 132m | 5.6652 | 0 | 1 | 1 | 2.2 | 132m | 2 | 2h | 2.2 | 132m | 2 | 2h
unit | 323_CC_1 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 323_CC_2 | 270m | 480m | 28.0467 | 0 | 1 | 1 | 4.5 | 270m | 5 | 5h | 8 | 480m | 8 | 8h
unit | 114_SYNC_COND_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 121_NUCLEAR_1 | 2880m | 1440m | 63.9998 | 0 | 1 | 1 | 48 | 2880m | 48 | 48h | 24 | 1440m | 24 | 24h
unit | 122_HYDRO_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 122_HYDRO_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 122_HYDRO_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 122_HYDRO_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 122_HYDRO_5 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 122_HYDRO_6 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 201_HYDRO_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 214_SYNC_COND_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 215_HYDRO_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 215_HYDRO_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 215_HYDRO_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 222_HYDRO_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 222_HYDRO_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 222_HYDRO_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 222_HYDRO_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 222_HYDRO_5 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 222_HYDRO_6 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 314_SYNC_COND_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 322_HYDRO_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 322_HYDRO_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 322_HYDRO_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 322_HYDRO_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 320_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 314_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 314_PV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 314_PV_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 314_PV_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_PV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 310_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 324_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 312_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 310_PV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 324_PV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 324_PV_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 113_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 319_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 215_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 102_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 101_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 102_PV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 104_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 212_CSP_1 | 60m | 60m | 10000 | 10000 | 1 | 1 | 1 | 60m | 1 | 1h | 1 | 60m | 1 | 1h
unit | 101_PV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 101_PV_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 101_PV_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 103_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 119_PV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 308_RTPV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_5 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_6 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_7 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_8 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_9 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_10 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_11 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_12 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 320_RTPV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 320_RTPV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 320_RTPV_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_RTPV_13 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 320_RTPV_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 320_RTPV_5 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_2 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_3 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_4 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_5 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_6 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 320_RTPV_6 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_7 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_8 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_9 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 118_RTPV_10 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 213_RTPV_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 309_WIND_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 317_WIND_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 303_WIND_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 122_WIND_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 313_STORAGE_1 | 0m | 0m | 0 | 0 | 1 | 1 | 0 | 0m | 0 | 0h | 0 | 0m | 0 | 0h
unit | 100_Dummy
unit | 200_Dummy
unit | 300_Dummy
unit | 100_Spill
unit | 200_Spill
unit | 300_Spill
unit | 212_CSP_1_Curtail

## rel_unit__node__direction
rel_class_name | unit | node | direction | parameter_name | value
unit__node__direction | 101_CT_1 | Region-1 | to_node | unit_capacity | 20 | Region-1
unit__node__direction | 101_CT_2 | Region-1 | to_node | unit_capacity | 20 | Region-1
unit__node__direction | 101_STEAM_3 | Region-1 | to_node | unit_capacity | 76 | Region-1
unit__node__direction | 101_STEAM_4 | Region-1 | to_node | unit_capacity | 76 | Region-1
unit__node__direction | 102_CT_1 | Region-1 | to_node | unit_capacity | 20 | Region-1
unit__node__direction | 102_CT_2 | Region-1 | to_node | unit_capacity | 20 | Region-1
unit__node__direction | 102_STEAM_3 | Region-1 | to_node | unit_capacity | 76 | Region-1
unit__node__direction | 102_STEAM_4 | Region-1 | to_node | unit_capacity | 76 | Region-1
unit__node__direction | 107_CC_1 | Region-1 | to_node | unit_capacity | 355 | Region-1
unit__node__direction | 113_CT_1 | Region-1 | to_node | unit_capacity | 55 | Region-1
unit__node__direction | 113_CT_2 | Region-1 | to_node | unit_capacity | 55 | Region-1
unit__node__direction | 113_CT_3 | Region-1 | to_node | unit_capacity | 55 | Region-1
unit__node__direction | 113_CT_4 | Region-1 | to_node | unit_capacity | 55 | Region-1
unit__node__direction | 115_STEAM_1 | Region-1 | to_node | unit_capacity | 12 | Region-1
unit__node__direction | 115_STEAM_2 | Region-1 | to_node | unit_capacity | 12 | Region-1
unit__node__direction | 115_STEAM_3 | Region-1 | to_node | unit_capacity | 155 | Region-1
unit__node__direction | 116_STEAM_1 | Region-1 | to_node | unit_capacity | 155 | Region-1
unit__node__direction | 118_CC_1 | Region-1 | to_node | unit_capacity | 355 | Region-1
unit__node__direction | 123_STEAM_2 | Region-1 | to_node | unit_capacity | 155 | Region-1
unit__node__direction | 123_STEAM_3 | Region-1 | to_node | unit_capacity | 350 | Region-1
unit__node__direction | 123_CT_1 | Region-1 | to_node | unit_capacity | 55 | Region-1
unit__node__direction | 123_CT_4 | Region-1 | to_node | unit_capacity | 55 | Region-1
unit__node__direction | 123_CT_5 | Region-1 | to_node | unit_capacity | 55 | Region-1
unit__node__direction | 201_CT_1 | Region-2 | to_node | unit_capacity | 20 | Region-2
unit__node__direction | 201_CT_2 | Region-2 | to_node | unit_capacity | 20 | Region-2
unit__node__direction | 201_STEAM_3 | Region-2 | to_node | unit_capacity | 76 | Region-2
unit__node__direction | 202_CT_1 | Region-2 | to_node | unit_capacity | 20 | Region-2
unit__node__direction | 202_CT_2 | Region-2 | to_node | unit_capacity | 20 | Region-2
unit__node__direction | 202_STEAM_3 | Region-2 | to_node | unit_capacity | 76 | Region-2
unit__node__direction | 202_STEAM_4 | Region-2 | to_node | unit_capacity | 76 | Region-2
unit__node__direction | 207_CT_1 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 207_CT_2 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 213_CC_3 | Region-2 | to_node | unit_capacity | 355 | Region-2
unit__node__direction | 213_CT_1 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 213_CT_2 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 215_CT_4 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 215_CT_5 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 216_STEAM_1 | Region-2 | to_node | unit_capacity | 155 | Region-2
unit__node__direction | 218_CC_1 | Region-2 | to_node | unit_capacity | 355 | Region-2
unit__node__direction | 221_CC_1 | Region-2 | to_node | unit_capacity | 355 | Region-2
unit__node__direction | 223_STEAM_1 | Region-2 | to_node | unit_capacity | 155 | Region-2
unit__node__direction | 223_STEAM_2 | Region-2 | to_node | unit_capacity | 155 | Region-2
unit__node__direction | 223_STEAM_3 | Region-2 | to_node | unit_capacity | 350 | Region-2
unit__node__direction | 223_CT_4 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 223_CT_5 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 223_CT_6 | Region-2 | to_node | unit_capacity | 55 | Region-2
unit__node__direction | 301_CT_1 | Region-3 | to_node | unit_capacity | 20 | Region-3
unit__node__direction | 301_CT_2 | Region-3 | to_node | unit_capacity | 20 | Region-3
unit__node__direction | 301_CT_3 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 301_CT_4 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 302_CT_1 | Region-3 | to_node | unit_capacity | 20 | Region-3
unit__node__direction | 302_CT_2 | Region-3 | to_node | unit_capacity | 20 | Region-3
unit__node__direction | 302_CT_3 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 302_CT_4 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 307_CT_1 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 307_CT_2 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 313_CC_1 | Region-3 | to_node | unit_capacity | 355 | Region-3
unit__node__direction | 315_STEAM_1 | Region-3 | to_node | unit_capacity | 12 | Region-3
unit__node__direction | 315_STEAM_2 | Region-3 | to_node | unit_capacity | 12 | Region-3
unit__node__direction | 315_STEAM_3 | Region-3 | to_node | unit_capacity | 12 | Region-3
unit__node__direction | 315_STEAM_4 | Region-3 | to_node | unit_capacity | 12 | Region-3
unit__node__direction | 315_STEAM_5 | Region-3 | to_node | unit_capacity | 12 | Region-3
unit__node__direction | 315_CT_6 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 315_CT_7 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 315_CT_8 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 316_STEAM_1 | Region-3 | to_node | unit_capacity | 155 | Region-3
unit__node__direction | 318_CC_1 | Region-3 | to_node | unit_capacity | 355 | Region-3
unit__node__direction | 321_CC_1 | Region-3 | to_node | unit_capacity | 355 | Region-3
unit__node__direction | 322_CT_5 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 322_CT_6 | Region-3 | to_node | unit_capacity | 55 | Region-3
unit__node__direction | 323_CC_1 | Region-3 | to_node | unit_capacity | 355 | Region-3
unit__node__direction | 323_CC_2 | Region-3 | to_node | unit_capacity | 355 | Region-3
unit__node__direction | 114_SYNC_COND_1 | Region-1 | to_node | unit_capacity | 0 | Region-1
unit__node__direction | 121_NUCLEAR_1 | Region-1 | to_node | unit_capacity | 400 | Region-1
unit__node__direction | 122_HYDRO_1 | Region-1 | to_node | unit_capacity | 50 | Region-1
unit__node__direction | 122_HYDRO_2 | Region-1 | to_node | unit_capacity | 50 | Region-1
unit__node__direction | 122_HYDRO_3 | Region-1 | to_node | unit_capacity | 50 | Region-1
unit__node__direction | 122_HYDRO_4 | Region-1 | to_node | unit_capacity | 50 | Region-1
unit__node__direction | 122_HYDRO_5 | Region-1 | to_node | unit_capacity | 50 | Region-1
unit__node__direction | 122_HYDRO_6 | Region-1 | to_node | unit_capacity | 50 | Region-1
unit__node__direction | 201_HYDRO_4 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 214_SYNC_COND_1 | Region-2 | to_node | unit_capacity | 0 | Region-2
unit__node__direction | 215_HYDRO_1 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 215_HYDRO_2 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 215_HYDRO_3 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 222_HYDRO_1 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 222_HYDRO_2 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 222_HYDRO_3 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 222_HYDRO_4 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 222_HYDRO_5 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 222_HYDRO_6 | Region-2 | to_node | unit_capacity | 50 | Region-2
unit__node__direction | 314_SYNC_COND_1 | Region-3 | to_node | unit_capacity | 0 | Region-3
unit__node__direction | 322_HYDRO_1 | Region-3 | to_node | unit_capacity | 50 | Region-3
unit__node__direction | 322_HYDRO_2 | Region-3 | to_node | unit_capacity | 50 | Region-3
unit__node__direction | 322_HYDRO_3 | Region-3 | to_node | unit_capacity | 50 | Region-3
unit__node__direction | 322_HYDRO_4 | Region-3 | to_node | unit_capacity | 50 | Region-3
unit__node__direction | 320_PV_1 | Region-3 | to_node | unit_capacity | 51.6 | Region-3
unit__node__direction | 314_PV_1 | Region-3 | to_node | unit_capacity | 51.6 | Region-3
unit__node__direction | 314_PV_2 | Region-3 | to_node | unit_capacity | 51.6 | Region-3
unit__node__direction | 313_PV_1 | Region-3 | to_node | unit_capacity | 95.1 | Region-3
unit__node__direction | 314_PV_3 | Region-3 | to_node | unit_capacity | 92.7 | Region-3
unit__node__direction | 314_PV_4 | Region-3 | to_node | unit_capacity | 51.6 | Region-3
unit__node__direction | 313_PV_2 | Region-3 | to_node | unit_capacity | 93.3 | Region-3
unit__node__direction | 310_PV_1 | Region-3 | to_node | unit_capacity | 51.7 | Region-3
unit__node__direction | 324_PV_1 | Region-3 | to_node | unit_capacity | 49.7 | Region-3
unit__node__direction | 312_PV_1 | Region-3 | to_node | unit_capacity | 94.1 | Region-3
unit__node__direction | 310_PV_2 | Region-3 | to_node | unit_capacity | 51.6 | Region-3
unit__node__direction | 324_PV_2 | Region-3 | to_node | unit_capacity | 51.6 | Region-3
unit__node__direction | 324_PV_3 | Region-3 | to_node | unit_capacity | 51 | Region-3
unit__node__direction | 113_PV_1 | Region-1 | to_node | unit_capacity | 93.6 | Region-1
unit__node__direction | 319_PV_1 | Region-3 | to_node | unit_capacity | 188.2 | Region-3
unit__node__direction | 215_PV_1 | Region-2 | to_node | unit_capacity | 125.1 | Region-2
unit__node__direction | 102_PV_1 | Region-1 | to_node | unit_capacity | 25.6 | Region-1
unit__node__direction | 101_PV_1 | Region-1 | to_node | unit_capacity | 25.9 | Region-1
unit__node__direction | 102_PV_2 | Region-1 | to_node | unit_capacity | 25.3 | Region-1
unit__node__direction | 104_PV_1 | Region-1 | to_node | unit_capacity | 26.8 | Region-1
unit__node__direction | 212_CSP_1 | Region-2 | to_node | unit_capacity | 200 | Region-2
unit__node__direction | 101_PV_2 | Region-1 | to_node | unit_capacity | 26.7 | Region-1
unit__node__direction | 101_PV_3 | Region-1 | to_node | unit_capacity | 26.2 | Region-1
unit__node__direction | 101_PV_4 | Region-1 | to_node | unit_capacity | 25.8 | Region-1
unit__node__direction | 103_PV_1 | Region-1 | to_node | unit_capacity | 61.5 | Region-1
unit__node__direction | 119_PV_1 | Region-1 | to_node | unit_capacity | 66.6 | Region-1
unit__node__direction | 308_RTPV_1 | Region-3 | to_node | unit_capacity | 100.9 | Region-3
unit__node__direction | 313_RTPV_1 | Region-3 | to_node | unit_capacity | 101.7 | Region-3
unit__node__direction | 313_RTPV_2 | Region-3 | to_node | unit_capacity | 63.1 | Region-3
unit__node__direction | 313_RTPV_3 | Region-3 | to_node | unit_capacity | 65.4 | Region-3
unit__node__direction | 313_RTPV_4 | Region-3 | to_node | unit_capacity | 67 | Region-3
unit__node__direction | 313_RTPV_5 | Region-3 | to_node | unit_capacity | 64.8 | Region-3
unit__node__direction | 313_RTPV_6 | Region-3 | to_node | unit_capacity | 63.8 | Region-3
unit__node__direction | 313_RTPV_7 | Region-3 | to_node | unit_capacity | 64.1 | Region-3
unit__node__direction | 313_RTPV_8 | Region-3 | to_node | unit_capacity | 66.6 | Region-3
unit__node__direction | 313_RTPV_9 | Region-3 | to_node | unit_capacity | 62.4 | Region-3
unit__node__direction | 313_RTPV_10 | Region-3 | to_node | unit_capacity | 66.9 | Region-3
unit__node__direction | 313_RTPV_11 | Region-3 | to_node | unit_capacity | 65.2 | Region-3
unit__node__direction | 313_RTPV_12 | Region-3 | to_node | unit_capacity | 27.8 | Region-3
unit__node__direction | 320_RTPV_1 | Region-3 | to_node | unit_capacity | 27.3 | Region-3
unit__node__direction | 320_RTPV_2 | Region-3 | to_node | unit_capacity | 27 | Region-3
unit__node__direction | 320_RTPV_3 | Region-3 | to_node | unit_capacity | 28.3 | Region-3
unit__node__direction | 313_RTPV_13 | Region-3 | to_node | unit_capacity | 27.2 | Region-3
unit__node__direction | 320_RTPV_4 | Region-3 | to_node | unit_capacity | 27 | Region-3
unit__node__direction | 320_RTPV_5 | Region-3 | to_node | unit_capacity | 28.2 | Region-3
unit__node__direction | 118_RTPV_1 | Region-1 | to_node | unit_capacity | 9.3 | Region-1
unit__node__direction | 118_RTPV_2 | Region-1 | to_node | unit_capacity | 9.7 | Region-1
unit__node__direction | 118_RTPV_3 | Region-1 | to_node | unit_capacity | 9.4 | Region-1
unit__node__direction | 118_RTPV_4 | Region-1 | to_node | unit_capacity | 9.1 | Region-1
unit__node__direction | 118_RTPV_5 | Region-1 | to_node | unit_capacity | 9.1 | Region-1
unit__node__direction | 118_RTPV_6 | Region-1 | to_node | unit_capacity | 9.7 | Region-1
unit__node__direction | 320_RTPV_6 | Region-3 | to_node | unit_capacity | 9.4 | Region-3
unit__node__direction | 118_RTPV_7 | Region-1 | to_node | unit_capacity | 11.8 | Region-1
unit__node__direction | 118_RTPV_8 | Region-1 | to_node | unit_capacity | 11.2 | Region-1
unit__node__direction | 118_RTPV_9 | Region-1 | to_node | unit_capacity | 10.3 | Region-1
unit__node__direction | 118_RTPV_10 | Region-1 | to_node | unit_capacity | 4.5 | Region-1
unit__node__direction | 213_RTPV_1 | Region-2 | to_node | unit_capacity | 13.2 | Region-2
unit__node__direction | 309_WIND_1 | Region-3 | to_node | unit_capacity | 148.3 | Region-3
unit__node__direction | 317_WIND_1 | Region-3 | to_node | unit_capacity | 799.1 | Region-3
unit__node__direction | 303_WIND_1 | Region-3 | to_node | unit_capacity | 847 | Region-3
unit__node__direction | 122_WIND_1 | Region-1 | to_node | unit_capacity | 713.5 | Region-1
unit__node__direction | 313_STORAGE_1 | Region-3 | to_node | unit_capacity | 50 | Region-3
unit__node__direction | 101_CT_1 | Region-1 | to_node | fuel_cost | 114.9032 | Region-1
unit__node__direction | 101_CT_2 | Region-1 | to_node | fuel_cost | 114.9032 | Region-1
unit__node__direction | 101_STEAM_3 | Region-1 | to_node | fuel_cost | 21.0068 | Region-1
unit__node__direction | 101_STEAM_4 | Region-1 | to_node | fuel_cost | 21.0068 | Region-1
unit__node__direction | 102_CT_1 | Region-1 | to_node | fuel_cost | 117.2463 | Region-1
unit__node__direction | 102_CT_2 | Region-1 | to_node | fuel_cost | 117.2463 | Region-1
unit__node__direction | 102_STEAM_3 | Region-1 | to_node | fuel_cost | 22.146 | Region-1
unit__node__direction | 102_STEAM_4 | Region-1 | to_node | fuel_cost | 22.146 | Region-1
unit__node__direction | 107_CC_1 | Region-1 | to_node | fuel_cost | 27.432 | Region-1
unit__node__direction | 113_CT_1 | Region-1 | to_node | fuel_cost | 37.7434 | Region-1
unit__node__direction | 113_CT_2 | Region-1 | to_node | fuel_cost | 37.7434 | Region-1
unit__node__direction | 113_CT_3 | Region-1 | to_node | fuel_cost | 37.7434 | Region-1
unit__node__direction | 113_CT_4 | Region-1 | to_node | fuel_cost | 37.7434 | Region-1
unit__node__direction | 115_STEAM_1 | Region-1 | to_node | fuel_cost | 149.2849 | Region-1
unit__node__direction | 115_STEAM_2 | Region-1 | to_node | fuel_cost | 149.2849 | Region-1
unit__node__direction | 115_STEAM_3 | Region-1 | to_node | fuel_cost | 23.6674 | Region-1
unit__node__direction | 116_STEAM_1 | Region-1 | to_node | fuel_cost | 24.201 | Region-1
unit__node__direction | 118_CC_1 | Region-1 | to_node | fuel_cost | 27.8908 | Region-1
unit__node__direction | 123_STEAM_2 | Region-1 | to_node | fuel_cost | 24.3604 | Region-1
unit__node__direction | 123_STEAM_3 | Region-1 | to_node | fuel_cost | 23.2505 | Region-1
unit__node__direction | 123_CT_1 | Region-1 | to_node | fuel_cost | 37.2178 | Region-1
unit__node__direction | 123_CT_4 | Region-1 | to_node | fuel_cost | 37.2178 | Region-1
unit__node__direction | 123_CT_5 | Region-1 | to_node | fuel_cost | 37.2178 | Region-1
unit__node__direction | 201_CT_1 | Region-2 | to_node | fuel_cost | 113.4543 | Region-2
unit__node__direction | 201_CT_2 | Region-2 | to_node | fuel_cost | 113.4543 | Region-2
unit__node__direction | 201_STEAM_3 | Region-2 | to_node | fuel_cost | 25.2421 | Region-2
unit__node__direction | 202_CT_1 | Region-2 | to_node | fuel_cost | 109.8237 | Region-2
unit__node__direction | 202_CT_2 | Region-2 | to_node | fuel_cost | 109.8237 | Region-2
unit__node__direction | 202_STEAM_3 | Region-2 | to_node | fuel_cost | 23.9432 | Region-2
unit__node__direction | 202_STEAM_4 | Region-2 | to_node | fuel_cost | 23.9432 | Region-2
unit__node__direction | 207_CT_1 | Region-2 | to_node | fuel_cost | 43.0253 | Region-2
unit__node__direction | 207_CT_2 | Region-2 | to_node | fuel_cost | 43.0253 | Region-2
unit__node__direction | 213_CC_3 | Region-2 | to_node | fuel_cost | 29.4615 | Region-2
unit__node__direction | 213_CT_1 | Region-2 | to_node | fuel_cost | 37.7434 | Region-2
unit__node__direction | 213_CT_2 | Region-2 | to_node | fuel_cost | 37.7434 | Region-2
unit__node__direction | 215_CT_4 | Region-2 | to_node | fuel_cost | 39.2874 | Region-2
unit__node__direction | 215_CT_5 | Region-2 | to_node | fuel_cost | 39.2874 | Region-2
unit__node__direction | 216_STEAM_1 | Region-2 | to_node | fuel_cost | 22.0159 | Region-2
unit__node__direction | 218_CC_1 | Region-2 | to_node | fuel_cost | 33.7667 | Region-2
unit__node__direction | 221_CC_1 | Region-2 | to_node | fuel_cost | 27.6856 | Region-2
unit__node__direction | 223_STEAM_1 | Region-2 | to_node | fuel_cost | 21.0093 | Region-2
unit__node__direction | 223_STEAM_2 | Region-2 | to_node | fuel_cost | 21.0093 | Region-2
unit__node__direction | 223_STEAM_3 | Region-2 | to_node | fuel_cost | 22.8049 | Region-2
unit__node__direction | 223_CT_4 | Region-2 | to_node | fuel_cost | 54.4864 | Region-2
unit__node__direction | 223_CT_5 | Region-2 | to_node | fuel_cost | 54.4864 | Region-2
unit__node__direction | 223_CT_6 | Region-2 | to_node | fuel_cost | 54.4864 | Region-2
unit__node__direction | 301_CT_1 | Region-3 | to_node | fuel_cost | 118.8753 | Region-3
unit__node__direction | 301_CT_2 | Region-3 | to_node | fuel_cost | 118.8753 | Region-3
unit__node__direction | 301_CT_3 | Region-3 | to_node | fuel_cost | 40.6533 | Region-3
unit__node__direction | 301_CT_4 | Region-3 | to_node | fuel_cost | 40.6533 | Region-3
unit__node__direction | 302_CT_1 | Region-3 | to_node | fuel_cost | 118.8753 | Region-3
unit__node__direction | 302_CT_2 | Region-3 | to_node | fuel_cost | 118.8753 | Region-3
unit__node__direction | 302_CT_3 | Region-3 | to_node | fuel_cost | 46.0993 | Region-3
unit__node__direction | 302_CT_4 | Region-3 | to_node | fuel_cost | 46.0993 | Region-3
unit__node__direction | 307_CT_1 | Region-3 | to_node | fuel_cost | 39.2804 | Region-3
unit__node__direction | 307_CT_2 | Region-3 | to_node | fuel_cost | 39.2804 | Region-3
unit__node__direction | 313_CC_1 | Region-3 | to_node | fuel_cost | 28.0126 | Region-3
unit__node__direction | 315_STEAM_1 | Region-3 | to_node | fuel_cost | 120.4604 | Region-3
unit__node__direction | 315_STEAM_2 | Region-3 | to_node | fuel_cost | 120.4604 | Region-3
unit__node__direction | 315_STEAM_3 | Region-3 | to_node | fuel_cost | 120.4604 | Region-3
unit__node__direction | 315_STEAM_4 | Region-3 | to_node | fuel_cost | 120.4604 | Region-3
unit__node__direction | 315_STEAM_5 | Region-3 | to_node | fuel_cost | 120.4604 | Region-3
unit__node__direction | 315_CT_6 | Region-3 | to_node | fuel_cost | 33.1113 | Region-3
unit__node__direction | 315_CT_7 | Region-3 | to_node | fuel_cost | 33.1113 | Region-3
unit__node__direction | 315_CT_8 | Region-3 | to_node | fuel_cost | 33.1113 | Region-3
unit__node__direction | 316_STEAM_1 | Region-3 | to_node | fuel_cost | 23.9528 | Region-3
unit__node__direction | 318_CC_1 | Region-3 | to_node | fuel_cost | 29.6809 | Region-3
unit__node__direction | 321_CC_1 | Region-3 | to_node | fuel_cost | 27.7992 | Region-3
unit__node__direction | 322_CT_5 | Region-3 | to_node | fuel_cost | 34.3039 | Region-3
unit__node__direction | 322_CT_6 | Region-3 | to_node | fuel_cost | 34.3039 | Region-3
unit__node__direction | 323_CC_1 | Region-3 | to_node | fuel_cost | 29.1014 | Region-3
unit__node__direction | 323_CC_2 | Region-3 | to_node | fuel_cost | 29.1014 | Region-3
unit__node__direction | 114_SYNC_COND_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 121_NUCLEAR_1 | Region-1 | to_node | fuel_cost | 8.1035 | Region-1
unit__node__direction | 122_HYDRO_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_2 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_3 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_4 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_5 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_6 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 201_HYDRO_4 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 214_SYNC_COND_1 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 215_HYDRO_1 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 215_HYDRO_2 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 215_HYDRO_3 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_1 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_2 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_3 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_4 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_5 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_6 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 314_SYNC_COND_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 322_HYDRO_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 322_HYDRO_2 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 322_HYDRO_3 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 322_HYDRO_4 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 320_PV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 314_PV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 314_PV_2 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_PV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 314_PV_3 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 314_PV_4 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_PV_2 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 310_PV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 324_PV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 312_PV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 310_PV_2 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 324_PV_2 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 324_PV_3 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 113_PV_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 319_PV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 215_PV_1 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 102_PV_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 101_PV_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 102_PV_2 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 104_PV_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 212_CSP_1 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 101_PV_2 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 101_PV_3 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 101_PV_4 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 103_PV_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 119_PV_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 308_RTPV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_2 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_3 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_4 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_5 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_6 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_7 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_8 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_9 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_10 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_11 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_12 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 320_RTPV_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 320_RTPV_2 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 320_RTPV_3 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_RTPV_13 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 320_RTPV_4 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 320_RTPV_5 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 118_RTPV_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 118_RTPV_2 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 118_RTPV_3 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 118_RTPV_4 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 118_RTPV_5 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 118_RTPV_6 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 320_RTPV_6 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 118_RTPV_7 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 118_RTPV_8 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 118_RTPV_9 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 118_RTPV_10 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 213_RTPV_1 | Region-2 | to_node | fuel_cost | 0 | Region-2
unit__node__direction | 309_WIND_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 317_WIND_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 303_WIND_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 122_WIND_1 | Region-1 | to_node | fuel_cost | 0 | Region-1
unit__node__direction | 313_STORAGE_1 | Region-3 | to_node | fuel_cost | 0 | Region-3
unit__node__direction | 101_CT_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 101_CT_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 101_STEAM_3 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 101_STEAM_4 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 102_CT_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 102_CT_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 102_STEAM_3 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 102_STEAM_4 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 107_CC_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 113_CT_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 113_CT_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 113_CT_3 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 113_CT_4 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 115_STEAM_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 115_STEAM_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 115_STEAM_3 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 116_STEAM_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_CC_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 123_STEAM_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 123_STEAM_3 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 123_CT_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 123_CT_4 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 123_CT_5 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 201_CT_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 201_CT_2 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 201_STEAM_3 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 202_CT_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 202_CT_2 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 202_STEAM_3 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 202_STEAM_4 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 207_CT_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 207_CT_2 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 213_CC_3 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 213_CT_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 213_CT_2 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 215_CT_4 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 215_CT_5 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 216_STEAM_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 218_CC_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 221_CC_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 223_STEAM_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 223_STEAM_2 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 223_STEAM_3 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 223_CT_4 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 223_CT_5 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 223_CT_6 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 301_CT_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 301_CT_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 301_CT_3 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 301_CT_4 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 302_CT_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 302_CT_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 302_CT_3 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 302_CT_4 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 307_CT_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 307_CT_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_CC_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 315_STEAM_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 315_STEAM_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 315_STEAM_3 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 315_STEAM_4 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 315_STEAM_5 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 315_CT_6 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 315_CT_7 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 315_CT_8 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 316_STEAM_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 318_CC_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 321_CC_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 322_CT_5 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 322_CT_6 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 323_CC_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 323_CC_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 114_SYNC_COND_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 121_NUCLEAR_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_3 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_4 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_5 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 122_HYDRO_6 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 201_HYDRO_4 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 214_SYNC_COND_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 215_HYDRO_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 215_HYDRO_2 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 215_HYDRO_3 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_2 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_3 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_4 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_5 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 222_HYDRO_6 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 314_SYNC_COND_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 322_HYDRO_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 322_HYDRO_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 322_HYDRO_3 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 322_HYDRO_4 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 320_PV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 314_PV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 314_PV_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_PV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 314_PV_3 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 314_PV_4 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_PV_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 310_PV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 324_PV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 312_PV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 310_PV_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 324_PV_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 324_PV_3 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 113_PV_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 319_PV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 215_PV_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 102_PV_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 101_PV_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 102_PV_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 104_PV_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 212_CSP_1 | Region-2 | to_node | vom_cost | 1100 | Region-2
unit__node__direction | 101_PV_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 101_PV_3 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 101_PV_4 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 103_PV_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 119_PV_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 308_RTPV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_3 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_4 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_5 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_6 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_7 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_8 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_9 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_10 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_11 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_12 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 320_RTPV_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 320_RTPV_2 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 320_RTPV_3 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 313_RTPV_13 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 320_RTPV_4 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 320_RTPV_5 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 118_RTPV_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_RTPV_2 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_RTPV_3 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_RTPV_4 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_RTPV_5 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_RTPV_6 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 320_RTPV_6 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 118_RTPV_7 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_RTPV_8 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_RTPV_9 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 118_RTPV_10 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 213_RTPV_1 | Region-2 | to_node | vom_cost | 0 | Region-2
unit__node__direction | 309_WIND_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 317_WIND_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 303_WIND_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 122_WIND_1 | Region-1 | to_node | vom_cost | 0 | Region-1
unit__node__direction | 313_STORAGE_1 | Region-3 | to_node | vom_cost | 0 | Region-3
unit__node__direction | 101_CT_1 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 101_CT_2 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 101_STEAM_3 | Region-1 | to_node | minimum_operating_point | 0.39474 | Region-1
unit__node__direction | 101_STEAM_4 | Region-1 | to_node | minimum_operating_point | 0.39474 | Region-1
unit__node__direction | 102_CT_1 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 102_CT_2 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 102_STEAM_3 | Region-1 | to_node | minimum_operating_point | 0.39474 | Region-1
unit__node__direction | 102_STEAM_4 | Region-1 | to_node | minimum_operating_point | 0.39474 | Region-1
unit__node__direction | 107_CC_1 | Region-1 | to_node | minimum_operating_point | 0.47887 | Region-1
unit__node__direction | 113_CT_1 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 113_CT_2 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 113_CT_3 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 113_CT_4 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 115_STEAM_1 | Region-1 | to_node | minimum_operating_point | 0.41667 | Region-1
unit__node__direction | 115_STEAM_2 | Region-1 | to_node | minimum_operating_point | 0.41667 | Region-1
unit__node__direction | 115_STEAM_3 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 116_STEAM_1 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 118_CC_1 | Region-1 | to_node | minimum_operating_point | 0.47887 | Region-1
unit__node__direction | 123_STEAM_2 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 123_STEAM_3 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 123_CT_1 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 123_CT_4 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 123_CT_5 | Region-1 | to_node | minimum_operating_point | 0.4 | Region-1
unit__node__direction | 201_CT_1 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 201_CT_2 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 201_STEAM_3 | Region-2 | to_node | minimum_operating_point | 0.39474 | Region-2
unit__node__direction | 202_CT_1 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 202_CT_2 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 202_STEAM_3 | Region-2 | to_node | minimum_operating_point | 0.39474 | Region-2
unit__node__direction | 202_STEAM_4 | Region-2 | to_node | minimum_operating_point | 0.39474 | Region-2
unit__node__direction | 207_CT_1 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 207_CT_2 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 213_CC_3 | Region-2 | to_node | minimum_operating_point | 0.47887 | Region-2
unit__node__direction | 213_CT_1 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 213_CT_2 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 215_CT_4 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 215_CT_5 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 216_STEAM_1 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 218_CC_1 | Region-2 | to_node | minimum_operating_point | 0.47887 | Region-2
unit__node__direction | 221_CC_1 | Region-2 | to_node | minimum_operating_point | 0.47887 | Region-2
unit__node__direction | 223_STEAM_1 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 223_STEAM_2 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 223_STEAM_3 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 223_CT_4 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 223_CT_5 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 223_CT_6 | Region-2 | to_node | minimum_operating_point | 0.4 | Region-2
unit__node__direction | 301_CT_1 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 301_CT_2 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 301_CT_3 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 301_CT_4 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 302_CT_1 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 302_CT_2 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 302_CT_3 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 302_CT_4 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 307_CT_1 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 307_CT_2 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 313_CC_1 | Region-3 | to_node | minimum_operating_point | 0.47887 | Region-3
unit__node__direction | 315_STEAM_1 | Region-3 | to_node | minimum_operating_point | 0.41667 | Region-3
unit__node__direction | 315_STEAM_2 | Region-3 | to_node | minimum_operating_point | 0.41667 | Region-3
unit__node__direction | 315_STEAM_3 | Region-3 | to_node | minimum_operating_point | 0.41667 | Region-3
unit__node__direction | 315_STEAM_4 | Region-3 | to_node | minimum_operating_point | 0.41667 | Region-3
unit__node__direction | 315_STEAM_5 | Region-3 | to_node | minimum_operating_point | 0.41667 | Region-3
unit__node__direction | 315_CT_6 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 315_CT_7 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 315_CT_8 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 316_STEAM_1 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 318_CC_1 | Region-3 | to_node | minimum_operating_point | 0.47887 | Region-3
unit__node__direction | 321_CC_1 | Region-3 | to_node | minimum_operating_point | 0.47887 | Region-3
unit__node__direction | 322_CT_5 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 322_CT_6 | Region-3 | to_node | minimum_operating_point | 0.4 | Region-3
unit__node__direction | 323_CC_1 | Region-3 | to_node | minimum_operating_point | 0.47887 | Region-3
unit__node__direction | 323_CC_2 | Region-3 | to_node | minimum_operating_point | 0.47887 | Region-3
unit__node__direction | 114_SYNC_COND_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 121_NUCLEAR_1 | Region-1 | to_node | minimum_operating_point | 0.99 | Region-1
unit__node__direction | 122_HYDRO_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 122_HYDRO_2 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 122_HYDRO_3 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 122_HYDRO_4 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 122_HYDRO_5 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 122_HYDRO_6 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 201_HYDRO_4 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 214_SYNC_COND_1 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 215_HYDRO_1 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 215_HYDRO_2 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 215_HYDRO_3 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 222_HYDRO_1 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 222_HYDRO_2 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 222_HYDRO_3 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 222_HYDRO_4 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 222_HYDRO_5 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 222_HYDRO_6 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 314_SYNC_COND_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 322_HYDRO_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 322_HYDRO_2 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 322_HYDRO_3 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 322_HYDRO_4 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 320_PV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 314_PV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 314_PV_2 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_PV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 314_PV_3 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 314_PV_4 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_PV_2 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 310_PV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 324_PV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 312_PV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 310_PV_2 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 324_PV_2 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 324_PV_3 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 113_PV_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 319_PV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 215_PV_1 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 102_PV_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 101_PV_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 102_PV_2 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 104_PV_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 212_CSP_1 | Region-2 | to_node | minimum_operating_point | 0.15 | Region-2
unit__node__direction | 101_PV_2 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 101_PV_3 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 101_PV_4 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 103_PV_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 119_PV_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 308_RTPV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_2 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_3 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_4 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_5 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_6 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_7 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_8 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_9 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_10 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_11 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_12 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 320_RTPV_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 320_RTPV_2 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 320_RTPV_3 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_RTPV_13 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 320_RTPV_4 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 320_RTPV_5 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 118_RTPV_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 118_RTPV_2 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 118_RTPV_3 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 118_RTPV_4 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 118_RTPV_5 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 118_RTPV_6 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 320_RTPV_6 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 118_RTPV_7 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 118_RTPV_8 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 118_RTPV_9 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 118_RTPV_10 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 213_RTPV_1 | Region-2 | to_node | minimum_operating_point | 0 | Region-2
unit__node__direction | 309_WIND_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 317_WIND_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 303_WIND_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 122_WIND_1 | Region-1 | to_node | minimum_operating_point | 0 | Region-1
unit__node__direction | 313_STORAGE_1 | Region-3 | to_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 313_STORAGE_1 | Region-3 | from_node | unit_capacity | 50 | Region-3
unit__node__direction | 313_STORAGE_1 | Region-3 | from_node | fuel_cost | 0 | Region-3
unit__node__direction | 313_STORAGE_1 | Region-3 | from_node | vom_cost | 0 | Region-3
unit__node__direction | 313_STORAGE_1 | Region-3 | from_node | minimum_operating_point | 0 | Region-3
unit__node__direction | 212_CSP_1 | RES_gen-212_CSP_1 | from_node
unit__node__direction | 320_PV_1 | RES_gen-320_PV_1 | from_node
unit__node__direction | 314_PV_1 | RES_gen-314_PV_1 | from_node
unit__node__direction | 314_PV_2 | RES_gen-314_PV_2 | from_node
unit__node__direction | 313_PV_1 | RES_gen-313_PV_1 | from_node
unit__node__direction | 314_PV_3 | RES_gen-314_PV_3 | from_node
unit__node__direction | 314_PV_4 | RES_gen-314_PV_4 | from_node
unit__node__direction | 313_PV_2 | RES_gen-313_PV_2 | from_node
unit__node__direction | 310_PV_1 | RES_gen-310_PV_1 | from_node
unit__node__direction | 324_PV_1 | RES_gen-324_PV_1 | from_node
unit__node__direction | 312_PV_1 | RES_gen-312_PV_1 | from_node
unit__node__direction | 310_PV_2 | RES_gen-310_PV_2 | from_node
unit__node__direction | 324_PV_2 | RES_gen-324_PV_2 | from_node
unit__node__direction | 324_PV_3 | RES_gen-324_PV_3 | from_node
unit__node__direction | 113_PV_1 | RES_gen-113_PV_1 | from_node
unit__node__direction | 319_PV_1 | RES_gen-319_PV_1 | from_node
unit__node__direction | 215_PV_1 | RES_gen-215_PV_1 | from_node
unit__node__direction | 102_PV_1 | RES_gen-102_PV_1 | from_node
unit__node__direction | 101_PV_1 | RES_gen-101_PV_1 | from_node
unit__node__direction | 102_PV_2 | RES_gen-102_PV_2 | from_node
unit__node__direction | 104_PV_1 | RES_gen-104_PV_1 | from_node
unit__node__direction | 101_PV_2 | RES_gen-101_PV_2 | from_node
unit__node__direction | 101_PV_3 | RES_gen-101_PV_3 | from_node
unit__node__direction | 101_PV_4 | RES_gen-101_PV_4 | from_node
unit__node__direction | 103_PV_1 | RES_gen-103_PV_1 | from_node
unit__node__direction | 119_PV_1 | RES_gen-119_PV_1 | from_node
unit__node__direction | 308_RTPV_1 | RES_gen-308_RTPV_1 | from_node
unit__node__direction | 313_RTPV_1 | RES_gen-313_RTPV_1 | from_node
unit__node__direction | 313_RTPV_2 | RES_gen-313_RTPV_2 | from_node
unit__node__direction | 313_RTPV_3 | RES_gen-313_RTPV_3 | from_node
unit__node__direction | 313_RTPV_4 | RES_gen-313_RTPV_4 | from_node
unit__node__direction | 313_RTPV_5 | RES_gen-313_RTPV_5 | from_node
unit__node__direction | 313_RTPV_6 | RES_gen-313_RTPV_6 | from_node
unit__node__direction | 313_RTPV_7 | RES_gen-313_RTPV_7 | from_node
unit__node__direction | 313_RTPV_8 | RES_gen-313_RTPV_8 | from_node
unit__node__direction | 313_RTPV_9 | RES_gen-313_RTPV_9 | from_node
unit__node__direction | 313_RTPV_10 | RES_gen-313_RTPV_10 | from_node
unit__node__direction | 313_RTPV_11 | RES_gen-313_RTPV_11 | from_node
unit__node__direction | 313_RTPV_12 | RES_gen-313_RTPV_12 | from_node
unit__node__direction | 320_RTPV_1 | RES_gen-320_RTPV_1 | from_node
unit__node__direction | 320_RTPV_2 | RES_gen-320_RTPV_2 | from_node
unit__node__direction | 320_RTPV_3 | RES_gen-320_RTPV_3 | from_node
unit__node__direction | 313_RTPV_13 | RES_gen-313_RTPV_13 | from_node
unit__node__direction | 320_RTPV_4 | RES_gen-320_RTPV_4 | from_node
unit__node__direction | 320_RTPV_5 | RES_gen-320_RTPV_5 | from_node
unit__node__direction | 118_RTPV_1 | RES_gen-118_RTPV_1 | from_node
unit__node__direction | 118_RTPV_2 | RES_gen-118_RTPV_2 | from_node
unit__node__direction | 118_RTPV_3 | RES_gen-118_RTPV_3 | from_node
unit__node__direction | 118_RTPV_4 | RES_gen-118_RTPV_4 | from_node
unit__node__direction | 118_RTPV_5 | RES_gen-118_RTPV_5 | from_node
unit__node__direction | 118_RTPV_6 | RES_gen-118_RTPV_6 | from_node
unit__node__direction | 320_RTPV_6 | RES_gen-320_RTPV_6 | from_node
unit__node__direction | 118_RTPV_7 | RES_gen-118_RTPV_7 | from_node
unit__node__direction | 118_RTPV_8 | RES_gen-118_RTPV_8 | from_node
unit__node__direction | 118_RTPV_9 | RES_gen-118_RTPV_9 | from_node
unit__node__direction | 118_RTPV_10 | RES_gen-118_RTPV_10 | from_node
unit__node__direction | 213_RTPV_1 | RES_gen-213_RTPV_1 | from_node
unit__node__direction | 309_WIND_1 | RES_gen-309_WIND_1 | from_node
unit__node__direction | 317_WIND_1 | RES_gen-317_WIND_1 | from_node
unit__node__direction | 303_WIND_1 | RES_gen-303_WIND_1 | from_node
unit__node__direction | 122_WIND_1 | RES_gen-122_WIND_1 | from_node
unit__node__direction | 122_HYDRO_1 | RES_gen-122_HYDRO_1 | from_node
unit__node__direction | 122_HYDRO_2 | RES_gen-122_HYDRO_2 | from_node
unit__node__direction | 122_HYDRO_3 | RES_gen-122_HYDRO_3 | from_node
unit__node__direction | 122_HYDRO_4 | RES_gen-122_HYDRO_4 | from_node
unit__node__direction | 122_HYDRO_5 | RES_gen-122_HYDRO_5 | from_node
unit__node__direction | 122_HYDRO_6 | RES_gen-122_HYDRO_6 | from_node
unit__node__direction | 201_HYDRO_4 | RES_gen-201_HYDRO_4 | from_node
unit__node__direction | 215_HYDRO_1 | RES_gen-215_HYDRO_1 | from_node
unit__node__direction | 215_HYDRO_2 | RES_gen-215_HYDRO_2 | from_node
unit__node__direction | 215_HYDRO_3 | RES_gen-215_HYDRO_3 | from_node
unit__node__direction | 222_HYDRO_1 | RES_gen-222_HYDRO_1 | from_node
unit__node__direction | 222_HYDRO_2 | RES_gen-222_HYDRO_2 | from_node
unit__node__direction | 222_HYDRO_3 | RES_gen-222_HYDRO_3 | from_node
unit__node__direction | 222_HYDRO_4 | RES_gen-222_HYDRO_4 | from_node
unit__node__direction | 222_HYDRO_5 | RES_gen-222_HYDRO_5 | from_node
unit__node__direction | 222_HYDRO_6 | RES_gen-222_HYDRO_6 | from_node
unit__node__direction | 322_HYDRO_1 | RES_gen-322_HYDRO_1 | from_node
unit__node__direction | 322_HYDRO_2 | RES_gen-322_HYDRO_2 | from_node
unit__node__direction | 322_HYDRO_3 | RES_gen-322_HYDRO_3 | from_node
unit__node__direction | 322_HYDRO_4 | RES_gen-322_HYDRO_4 | from_node
unit__node__direction | 100_Dummy | Region-1 | to_node
unit__node__direction | 200_Dummy | Region-2 | to_node
unit__node__direction | 300_Dummy | Region-3 | to_node
unit__node__direction | 100_Spill | Region-1 | from_node
unit__node__direction | 200_Spill | Region-2 | from_node
unit__node__direction | 300_Spill | Region-3 | from_node
unit__node__direction | 212_CSP_1_Curtail | RES_gen-212_CSP_1 | from_node
unit__commodity__direction | 100_Dummy | Region-1 | to_node | fuel_cost | 2000
unit__commodity__direction | 200_Dummy | Region-2 | to_node | fuel_cost | 2000
unit__commodity__direction | 300_Dummy | Region-3 | to_node | fuel_cost | 2000
unit__commodity__direction | 100_Spill | Region-1 | from_node
unit__commodity__direction | 200_Spill | Region-2 | from_node
unit__commodity__direction | 300_Spill | Region-3 | from_node

## rel_u__n__d-bus_detailed
rel_class_name | unit | node | direction | parameter_name | value
unit__node__direction | 101_CT_1 | bus-101 | to_node | unit_capacity | 20 | bus-101
unit__node__direction | 101_CT_2 | bus-101 | to_node | unit_capacity | 20 | bus-101
unit__node__direction | 101_STEAM_3 | bus-101 | to_node | unit_capacity | 76 | bus-101
unit__node__direction | 101_STEAM_4 | bus-101 | to_node | unit_capacity | 76 | bus-101
unit__node__direction | 102_CT_1 | bus-102 | to_node | unit_capacity | 20 | bus-102
unit__node__direction | 102_CT_2 | bus-102 | to_node | unit_capacity | 20 | bus-102
unit__node__direction | 102_STEAM_3 | bus-102 | to_node | unit_capacity | 76 | bus-102
unit__node__direction | 102_STEAM_4 | bus-102 | to_node | unit_capacity | 76 | bus-102
unit__node__direction | 107_CC_1 | bus-107 | to_node | unit_capacity | 355 | bus-107
unit__node__direction | 113_CT_1 | bus-113 | to_node | unit_capacity | 55 | bus-113
unit__node__direction | 113_CT_2 | bus-113 | to_node | unit_capacity | 55 | bus-113
unit__node__direction | 113_CT_3 | bus-113 | to_node | unit_capacity | 55 | bus-113
unit__node__direction | 113_CT_4 | bus-113 | to_node | unit_capacity | 55 | bus-113
unit__node__direction | 115_STEAM_1 | bus-115 | to_node | unit_capacity | 12 | bus-115
unit__node__direction | 115_STEAM_2 | bus-115 | to_node | unit_capacity | 12 | bus-115
unit__node__direction | 115_STEAM_3 | bus-115 | to_node | unit_capacity | 155 | bus-115
unit__node__direction | 116_STEAM_1 | bus-116 | to_node | unit_capacity | 155 | bus-116
unit__node__direction | 118_CC_1 | bus-118 | to_node | unit_capacity | 355 | bus-118
unit__node__direction | 123_STEAM_2 | bus-123 | to_node | unit_capacity | 155 | bus-123
unit__node__direction | 123_STEAM_3 | bus-123 | to_node | unit_capacity | 350 | bus-123
unit__node__direction | 123_CT_1 | bus-123 | to_node | unit_capacity | 55 | bus-123
unit__node__direction | 123_CT_4 | bus-123 | to_node | unit_capacity | 55 | bus-123
unit__node__direction | 123_CT_5 | bus-123 | to_node | unit_capacity | 55 | bus-123
unit__node__direction | 201_CT_1 | bus-201 | to_node | unit_capacity | 20 | bus-201
unit__node__direction | 201_CT_2 | bus-201 | to_node | unit_capacity | 20 | bus-201
unit__node__direction | 201_STEAM_3 | bus-201 | to_node | unit_capacity | 76 | bus-201
unit__node__direction | 202_CT_1 | bus-202 | to_node | unit_capacity | 20 | bus-202
unit__node__direction | 202_CT_2 | bus-202 | to_node | unit_capacity | 20 | bus-202
unit__node__direction | 202_STEAM_3 | bus-202 | to_node | unit_capacity | 76 | bus-202
unit__node__direction | 202_STEAM_4 | bus-202 | to_node | unit_capacity | 76 | bus-202
unit__node__direction | 207_CT_1 | bus-207 | to_node | unit_capacity | 55 | bus-207
unit__node__direction | 207_CT_2 | bus-207 | to_node | unit_capacity | 55 | bus-207
unit__node__direction | 213_CC_3 | bus-213 | to_node | unit_capacity | 355 | bus-213
unit__node__direction | 213_CT_1 | bus-213 | to_node | unit_capacity | 55 | bus-213
unit__node__direction | 213_CT_2 | bus-213 | to_node | unit_capacity | 55 | bus-213
unit__node__direction | 215_CT_4 | bus-215 | to_node | unit_capacity | 55 | bus-215
unit__node__direction | 215_CT_5 | bus-215 | to_node | unit_capacity | 55 | bus-215
unit__node__direction | 216_STEAM_1 | bus-216 | to_node | unit_capacity | 155 | bus-216
unit__node__direction | 218_CC_1 | bus-218 | to_node | unit_capacity | 355 | bus-218
unit__node__direction | 221_CC_1 | bus-221 | to_node | unit_capacity | 355 | bus-221
unit__node__direction | 223_STEAM_1 | bus-223 | to_node | unit_capacity | 155 | bus-223
unit__node__direction | 223_STEAM_2 | bus-223 | to_node | unit_capacity | 155 | bus-223
unit__node__direction | 223_STEAM_3 | bus-223 | to_node | unit_capacity | 350 | bus-223
unit__node__direction | 223_CT_4 | bus-223 | to_node | unit_capacity | 55 | bus-223
unit__node__direction | 223_CT_5 | bus-223 | to_node | unit_capacity | 55 | bus-223
unit__node__direction | 223_CT_6 | bus-223 | to_node | unit_capacity | 55 | bus-223
unit__node__direction | 301_CT_1 | bus-301 | to_node | unit_capacity | 20 | bus-301
unit__node__direction | 301_CT_2 | bus-301 | to_node | unit_capacity | 20 | bus-301
unit__node__direction | 301_CT_3 | bus-301 | to_node | unit_capacity | 55 | bus-301
unit__node__direction | 301_CT_4 | bus-301 | to_node | unit_capacity | 55 | bus-301
unit__node__direction | 302_CT_1 | bus-302 | to_node | unit_capacity | 20 | bus-302
unit__node__direction | 302_CT_2 | bus-302 | to_node | unit_capacity | 20 | bus-302
unit__node__direction | 302_CT_3 | bus-302 | to_node | unit_capacity | 55 | bus-302
unit__node__direction | 302_CT_4 | bus-302 | to_node | unit_capacity | 55 | bus-302
unit__node__direction | 307_CT_1 | bus-307 | to_node | unit_capacity | 55 | bus-307
unit__node__direction | 307_CT_2 | bus-307 | to_node | unit_capacity | 55 | bus-307
unit__node__direction | 313_CC_1 | bus-313 | to_node | unit_capacity | 355 | bus-313
unit__node__direction | 315_STEAM_1 | bus-315 | to_node | unit_capacity | 12 | bus-315
unit__node__direction | 315_STEAM_2 | bus-315 | to_node | unit_capacity | 12 | bus-315
unit__node__direction | 315_STEAM_3 | bus-315 | to_node | unit_capacity | 12 | bus-315
unit__node__direction | 315_STEAM_4 | bus-315 | to_node | unit_capacity | 12 | bus-315
unit__node__direction | 315_STEAM_5 | bus-315 | to_node | unit_capacity | 12 | bus-315
unit__node__direction | 315_CT_6 | bus-315 | to_node | unit_capacity | 55 | bus-315
unit__node__direction | 315_CT_7 | bus-315 | to_node | unit_capacity | 55 | bus-315
unit__node__direction | 315_CT_8 | bus-315 | to_node | unit_capacity | 55 | bus-315
unit__node__direction | 316_STEAM_1 | bus-316 | to_node | unit_capacity | 155 | bus-316
unit__node__direction | 318_CC_1 | bus-318 | to_node | unit_capacity | 355 | bus-318
unit__node__direction | 321_CC_1 | bus-321 | to_node | unit_capacity | 355 | bus-321
unit__node__direction | 322_CT_5 | bus-322 | to_node | unit_capacity | 55 | bus-322
unit__node__direction | 322_CT_6 | bus-322 | to_node | unit_capacity | 55 | bus-322
unit__node__direction | 323_CC_1 | bus-323 | to_node | unit_capacity | 355 | bus-323
unit__node__direction | 323_CC_2 | bus-323 | to_node | unit_capacity | 355 | bus-323
unit__node__direction | 114_SYNC_COND_1 | bus-114 | to_node | unit_capacity | 0 | bus-114
unit__node__direction | 121_NUCLEAR_1 | bus-121 | to_node | unit_capacity | 400 | bus-121
unit__node__direction | 122_HYDRO_1 | bus-122 | to_node | unit_capacity | 50 | bus-122
unit__node__direction | 122_HYDRO_2 | bus-122 | to_node | unit_capacity | 50 | bus-122
unit__node__direction | 122_HYDRO_3 | bus-122 | to_node | unit_capacity | 50 | bus-122
unit__node__direction | 122_HYDRO_4 | bus-122 | to_node | unit_capacity | 50 | bus-122
unit__node__direction | 122_HYDRO_5 | bus-122 | to_node | unit_capacity | 50 | bus-122
unit__node__direction | 122_HYDRO_6 | bus-122 | to_node | unit_capacity | 50 | bus-122
unit__node__direction | 201_HYDRO_4 | bus-201 | to_node | unit_capacity | 50 | bus-201
unit__node__direction | 214_SYNC_COND_1 | bus-214 | to_node | unit_capacity | 0 | bus-214
unit__node__direction | 215_HYDRO_1 | bus-215 | to_node | unit_capacity | 50 | bus-215
unit__node__direction | 215_HYDRO_2 | bus-215 | to_node | unit_capacity | 50 | bus-215
unit__node__direction | 215_HYDRO_3 | bus-215 | to_node | unit_capacity | 50 | bus-215
unit__node__direction | 222_HYDRO_1 | bus-222 | to_node | unit_capacity | 50 | bus-222
unit__node__direction | 222_HYDRO_2 | bus-222 | to_node | unit_capacity | 50 | bus-222
unit__node__direction | 222_HYDRO_3 | bus-222 | to_node | unit_capacity | 50 | bus-222
unit__node__direction | 222_HYDRO_4 | bus-222 | to_node | unit_capacity | 50 | bus-222
unit__node__direction | 222_HYDRO_5 | bus-222 | to_node | unit_capacity | 50 | bus-222
unit__node__direction | 222_HYDRO_6 | bus-222 | to_node | unit_capacity | 50 | bus-222
unit__node__direction | 314_SYNC_COND_1 | bus-314 | to_node | unit_capacity | 0 | bus-314
unit__node__direction | 322_HYDRO_1 | bus-322 | to_node | unit_capacity | 50 | bus-322
unit__node__direction | 322_HYDRO_2 | bus-322 | to_node | unit_capacity | 50 | bus-322
unit__node__direction | 322_HYDRO_3 | bus-322 | to_node | unit_capacity | 50 | bus-322
unit__node__direction | 322_HYDRO_4 | bus-322 | to_node | unit_capacity | 50 | bus-322
unit__node__direction | 320_PV_1 | bus-320 | to_node | unit_capacity | 51.6 | bus-320
unit__node__direction | 314_PV_1 | bus-314 | to_node | unit_capacity | 51.6 | bus-314
unit__node__direction | 314_PV_2 | bus-314 | to_node | unit_capacity | 51.6 | bus-314
unit__node__direction | 313_PV_1 | bus-313 | to_node | unit_capacity | 95.1 | bus-313
unit__node__direction | 314_PV_3 | bus-314 | to_node | unit_capacity | 92.7 | bus-314
unit__node__direction | 314_PV_4 | bus-314 | to_node | unit_capacity | 51.6 | bus-314
unit__node__direction | 313_PV_2 | bus-313 | to_node | unit_capacity | 93.3 | bus-313
unit__node__direction | 310_PV_1 | bus-310 | to_node | unit_capacity | 51.7 | bus-310
unit__node__direction | 324_PV_1 | bus-324 | to_node | unit_capacity | 49.7 | bus-324
unit__node__direction | 312_PV_1 | bus-312 | to_node | unit_capacity | 94.1 | bus-312
unit__node__direction | 310_PV_2 | bus-310 | to_node | unit_capacity | 51.6 | bus-310
unit__node__direction | 324_PV_2 | bus-324 | to_node | unit_capacity | 51.6 | bus-324
unit__node__direction | 324_PV_3 | bus-324 | to_node | unit_capacity | 51 | bus-324
unit__node__direction | 113_PV_1 | bus-113 | to_node | unit_capacity | 93.6 | bus-113
unit__node__direction | 319_PV_1 | bus-319 | to_node | unit_capacity | 188.2 | bus-319
unit__node__direction | 215_PV_1 | bus-215 | to_node | unit_capacity | 125.1 | bus-215
unit__node__direction | 102_PV_1 | bus-102 | to_node | unit_capacity | 25.6 | bus-102
unit__node__direction | 101_PV_1 | bus-101 | to_node | unit_capacity | 25.9 | bus-101
unit__node__direction | 102_PV_2 | bus-102 | to_node | unit_capacity | 25.3 | bus-102
unit__node__direction | 104_PV_1 | bus-104 | to_node | unit_capacity | 26.8 | bus-104
unit__node__direction | 212_CSP_1 | bus-212 | to_node | unit_capacity | 200 | bus-212
unit__node__direction | 101_PV_2 | bus-101 | to_node | unit_capacity | 26.7 | bus-101
unit__node__direction | 101_PV_3 | bus-101 | to_node | unit_capacity | 26.2 | bus-101
unit__node__direction | 101_PV_4 | bus-101 | to_node | unit_capacity | 25.8 | bus-101
unit__node__direction | 103_PV_1 | bus-103 | to_node | unit_capacity | 61.5 | bus-103
unit__node__direction | 119_PV_1 | bus-119 | to_node | unit_capacity | 66.6 | bus-119
unit__node__direction | 308_RTPV_1 | bus-308 | to_node | unit_capacity | 100.9 | bus-308
unit__node__direction | 313_RTPV_1 | bus-313 | to_node | unit_capacity | 101.7 | bus-313
unit__node__direction | 313_RTPV_2 | bus-313 | to_node | unit_capacity | 63.1 | bus-313
unit__node__direction | 313_RTPV_3 | bus-313 | to_node | unit_capacity | 65.4 | bus-313
unit__node__direction | 313_RTPV_4 | bus-313 | to_node | unit_capacity | 67 | bus-313
unit__node__direction | 313_RTPV_5 | bus-313 | to_node | unit_capacity | 64.8 | bus-313
unit__node__direction | 313_RTPV_6 | bus-313 | to_node | unit_capacity | 63.8 | bus-313
unit__node__direction | 313_RTPV_7 | bus-313 | to_node | unit_capacity | 64.1 | bus-313
unit__node__direction | 313_RTPV_8 | bus-313 | to_node | unit_capacity | 66.6 | bus-313
unit__node__direction | 313_RTPV_9 | bus-313 | to_node | unit_capacity | 62.4 | bus-313
unit__node__direction | 313_RTPV_10 | bus-313 | to_node | unit_capacity | 66.9 | bus-313
unit__node__direction | 313_RTPV_11 | bus-313 | to_node | unit_capacity | 65.2 | bus-313
unit__node__direction | 313_RTPV_12 | bus-313 | to_node | unit_capacity | 27.8 | bus-313
unit__node__direction | 320_RTPV_1 | bus-320 | to_node | unit_capacity | 27.3 | bus-320
unit__node__direction | 320_RTPV_2 | bus-320 | to_node | unit_capacity | 27 | bus-320
unit__node__direction | 320_RTPV_3 | bus-320 | to_node | unit_capacity | 28.3 | bus-320
unit__node__direction | 313_RTPV_13 | bus-313 | to_node | unit_capacity | 27.2 | bus-313
unit__node__direction | 320_RTPV_4 | bus-320 | to_node | unit_capacity | 27 | bus-320
unit__node__direction | 320_RTPV_5 | bus-320 | to_node | unit_capacity | 28.2 | bus-320
unit__node__direction | 118_RTPV_1 | bus-118 | to_node | unit_capacity | 9.3 | bus-118
unit__node__direction | 118_RTPV_2 | bus-118 | to_node | unit_capacity | 9.7 | bus-118
unit__node__direction | 118_RTPV_3 | bus-118 | to_node | unit_capacity | 9.4 | bus-118
unit__node__direction | 118_RTPV_4 | bus-118 | to_node | unit_capacity | 9.1 | bus-118
unit__node__direction | 118_RTPV_5 | bus-118 | to_node | unit_capacity | 9.1 | bus-118
unit__node__direction | 118_RTPV_6 | bus-118 | to_node | unit_capacity | 9.7 | bus-118
unit__node__direction | 320_RTPV_6 | bus-320 | to_node | unit_capacity | 9.4 | bus-320
unit__node__direction | 118_RTPV_7 | bus-118 | to_node | unit_capacity | 11.8 | bus-118
unit__node__direction | 118_RTPV_8 | bus-118 | to_node | unit_capacity | 11.2 | bus-118
unit__node__direction | 118_RTPV_9 | bus-118 | to_node | unit_capacity | 10.3 | bus-118
unit__node__direction | 118_RTPV_10 | bus-118 | to_node | unit_capacity | 4.5 | bus-118
unit__node__direction | 213_RTPV_1 | bus-213 | to_node | unit_capacity | 13.2 | bus-213
unit__node__direction | 309_WIND_1 | bus-309 | to_node | unit_capacity | 148.3 | bus-309
unit__node__direction | 317_WIND_1 | bus-317 | to_node | unit_capacity | 799.1 | bus-317
unit__node__direction | 303_WIND_1 | bus-303 | to_node | unit_capacity | 847 | bus-303
unit__node__direction | 122_WIND_1 | bus-122 | to_node | unit_capacity | 713.5 | bus-122
unit__node__direction | 313_STORAGE_1 | bus-313 | to_node | unit_capacity | 50 | bus-313
unit__node__direction | 101_CT_1 | bus-101 | to_node | fuel_cost | 114.9032 | bus-101
unit__node__direction | 101_CT_2 | bus-101 | to_node | fuel_cost | 114.9032 | bus-101
unit__node__direction | 101_STEAM_3 | bus-101 | to_node | fuel_cost | 21.0068 | bus-101
unit__node__direction | 101_STEAM_4 | bus-101 | to_node | fuel_cost | 21.0068 | bus-101
unit__node__direction | 102_CT_1 | bus-102 | to_node | fuel_cost | 117.2463 | bus-102
unit__node__direction | 102_CT_2 | bus-102 | to_node | fuel_cost | 117.2463 | bus-102
unit__node__direction | 102_STEAM_3 | bus-102 | to_node | fuel_cost | 22.146 | bus-102
unit__node__direction | 102_STEAM_4 | bus-102 | to_node | fuel_cost | 22.146 | bus-102
unit__node__direction | 107_CC_1 | bus-107 | to_node | fuel_cost | 27.432 | bus-107
unit__node__direction | 113_CT_1 | bus-113 | to_node | fuel_cost | 37.7434 | bus-113
unit__node__direction | 113_CT_2 | bus-113 | to_node | fuel_cost | 37.7434 | bus-113
unit__node__direction | 113_CT_3 | bus-113 | to_node | fuel_cost | 37.7434 | bus-113
unit__node__direction | 113_CT_4 | bus-113 | to_node | fuel_cost | 37.7434 | bus-113
unit__node__direction | 115_STEAM_1 | bus-115 | to_node | fuel_cost | 149.2849 | bus-115
unit__node__direction | 115_STEAM_2 | bus-115 | to_node | fuel_cost | 149.2849 | bus-115
unit__node__direction | 115_STEAM_3 | bus-115 | to_node | fuel_cost | 23.6674 | bus-115
unit__node__direction | 116_STEAM_1 | bus-116 | to_node | fuel_cost | 24.201 | bus-116
unit__node__direction | 118_CC_1 | bus-118 | to_node | fuel_cost | 27.8908 | bus-118
unit__node__direction | 123_STEAM_2 | bus-123 | to_node | fuel_cost | 24.3604 | bus-123
unit__node__direction | 123_STEAM_3 | bus-123 | to_node | fuel_cost | 23.2505 | bus-123
unit__node__direction | 123_CT_1 | bus-123 | to_node | fuel_cost | 37.2178 | bus-123
unit__node__direction | 123_CT_4 | bus-123 | to_node | fuel_cost | 37.2178 | bus-123
unit__node__direction | 123_CT_5 | bus-123 | to_node | fuel_cost | 37.2178 | bus-123
unit__node__direction | 201_CT_1 | bus-201 | to_node | fuel_cost | 113.4543 | bus-201
unit__node__direction | 201_CT_2 | bus-201 | to_node | fuel_cost | 113.4543 | bus-201
unit__node__direction | 201_STEAM_3 | bus-201 | to_node | fuel_cost | 25.2421 | bus-201
unit__node__direction | 202_CT_1 | bus-202 | to_node | fuel_cost | 109.8237 | bus-202
unit__node__direction | 202_CT_2 | bus-202 | to_node | fuel_cost | 109.8237 | bus-202
unit__node__direction | 202_STEAM_3 | bus-202 | to_node | fuel_cost | 23.9432 | bus-202
unit__node__direction | 202_STEAM_4 | bus-202 | to_node | fuel_cost | 23.9432 | bus-202
unit__node__direction | 207_CT_1 | bus-207 | to_node | fuel_cost | 43.0253 | bus-207
unit__node__direction | 207_CT_2 | bus-207 | to_node | fuel_cost | 43.0253 | bus-207
unit__node__direction | 213_CC_3 | bus-213 | to_node | fuel_cost | 29.4615 | bus-213
unit__node__direction | 213_CT_1 | bus-213 | to_node | fuel_cost | 37.7434 | bus-213
unit__node__direction | 213_CT_2 | bus-213 | to_node | fuel_cost | 37.7434 | bus-213
unit__node__direction | 215_CT_4 | bus-215 | to_node | fuel_cost | 39.2874 | bus-215
unit__node__direction | 215_CT_5 | bus-215 | to_node | fuel_cost | 39.2874 | bus-215
unit__node__direction | 216_STEAM_1 | bus-216 | to_node | fuel_cost | 22.0159 | bus-216
unit__node__direction | 218_CC_1 | bus-218 | to_node | fuel_cost | 33.7667 | bus-218
unit__node__direction | 221_CC_1 | bus-221 | to_node | fuel_cost | 27.6856 | bus-221
unit__node__direction | 223_STEAM_1 | bus-223 | to_node | fuel_cost | 21.0093 | bus-223
unit__node__direction | 223_STEAM_2 | bus-223 | to_node | fuel_cost | 21.0093 | bus-223
unit__node__direction | 223_STEAM_3 | bus-223 | to_node | fuel_cost | 22.8049 | bus-223
unit__node__direction | 223_CT_4 | bus-223 | to_node | fuel_cost | 54.4864 | bus-223
unit__node__direction | 223_CT_5 | bus-223 | to_node | fuel_cost | 54.4864 | bus-223
unit__node__direction | 223_CT_6 | bus-223 | to_node | fuel_cost | 54.4864 | bus-223
unit__node__direction | 301_CT_1 | bus-301 | to_node | fuel_cost | 118.8753 | bus-301
unit__node__direction | 301_CT_2 | bus-301 | to_node | fuel_cost | 118.8753 | bus-301
unit__node__direction | 301_CT_3 | bus-301 | to_node | fuel_cost | 40.6533 | bus-301
unit__node__direction | 301_CT_4 | bus-301 | to_node | fuel_cost | 40.6533 | bus-301
unit__node__direction | 302_CT_1 | bus-302 | to_node | fuel_cost | 118.8753 | bus-302
unit__node__direction | 302_CT_2 | bus-302 | to_node | fuel_cost | 118.8753 | bus-302
unit__node__direction | 302_CT_3 | bus-302 | to_node | fuel_cost | 46.0993 | bus-302
unit__node__direction | 302_CT_4 | bus-302 | to_node | fuel_cost | 46.0993 | bus-302
unit__node__direction | 307_CT_1 | bus-307 | to_node | fuel_cost | 39.2804 | bus-307
unit__node__direction | 307_CT_2 | bus-307 | to_node | fuel_cost | 39.2804 | bus-307
unit__node__direction | 313_CC_1 | bus-313 | to_node | fuel_cost | 28.0126 | bus-313
unit__node__direction | 315_STEAM_1 | bus-315 | to_node | fuel_cost | 120.4604 | bus-315
unit__node__direction | 315_STEAM_2 | bus-315 | to_node | fuel_cost | 120.4604 | bus-315
unit__node__direction | 315_STEAM_3 | bus-315 | to_node | fuel_cost | 120.4604 | bus-315
unit__node__direction | 315_STEAM_4 | bus-315 | to_node | fuel_cost | 120.4604 | bus-315
unit__node__direction | 315_STEAM_5 | bus-315 | to_node | fuel_cost | 120.4604 | bus-315
unit__node__direction | 315_CT_6 | bus-315 | to_node | fuel_cost | 33.1113 | bus-315
unit__node__direction | 315_CT_7 | bus-315 | to_node | fuel_cost | 33.1113 | bus-315
unit__node__direction | 315_CT_8 | bus-315 | to_node | fuel_cost | 33.1113 | bus-315
unit__node__direction | 316_STEAM_1 | bus-316 | to_node | fuel_cost | 23.9528 | bus-316
unit__node__direction | 318_CC_1 | bus-318 | to_node | fuel_cost | 29.6809 | bus-318
unit__node__direction | 321_CC_1 | bus-321 | to_node | fuel_cost | 27.7992 | bus-321
unit__node__direction | 322_CT_5 | bus-322 | to_node | fuel_cost | 34.3039 | bus-322
unit__node__direction | 322_CT_6 | bus-322 | to_node | fuel_cost | 34.3039 | bus-322
unit__node__direction | 323_CC_1 | bus-323 | to_node | fuel_cost | 29.1014 | bus-323
unit__node__direction | 323_CC_2 | bus-323 | to_node | fuel_cost | 29.1014 | bus-323
unit__node__direction | 114_SYNC_COND_1 | bus-114 | to_node | fuel_cost | 0 | bus-114
unit__node__direction | 121_NUCLEAR_1 | bus-121 | to_node | fuel_cost | 8.1035 | bus-121
unit__node__direction | 122_HYDRO_1 | bus-122 | to_node | fuel_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_2 | bus-122 | to_node | fuel_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_3 | bus-122 | to_node | fuel_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_4 | bus-122 | to_node | fuel_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_5 | bus-122 | to_node | fuel_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_6 | bus-122 | to_node | fuel_cost | 0 | bus-122
unit__node__direction | 201_HYDRO_4 | bus-201 | to_node | fuel_cost | 0 | bus-201
unit__node__direction | 214_SYNC_COND_1 | bus-214 | to_node | fuel_cost | 0 | bus-214
unit__node__direction | 215_HYDRO_1 | bus-215 | to_node | fuel_cost | 0 | bus-215
unit__node__direction | 215_HYDRO_2 | bus-215 | to_node | fuel_cost | 0 | bus-215
unit__node__direction | 215_HYDRO_3 | bus-215 | to_node | fuel_cost | 0 | bus-215
unit__node__direction | 222_HYDRO_1 | bus-222 | to_node | fuel_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_2 | bus-222 | to_node | fuel_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_3 | bus-222 | to_node | fuel_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_4 | bus-222 | to_node | fuel_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_5 | bus-222 | to_node | fuel_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_6 | bus-222 | to_node | fuel_cost | 0 | bus-222
unit__node__direction | 314_SYNC_COND_1 | bus-314 | to_node | fuel_cost | 0 | bus-314
unit__node__direction | 322_HYDRO_1 | bus-322 | to_node | fuel_cost | 0 | bus-322
unit__node__direction | 322_HYDRO_2 | bus-322 | to_node | fuel_cost | 0 | bus-322
unit__node__direction | 322_HYDRO_3 | bus-322 | to_node | fuel_cost | 0 | bus-322
unit__node__direction | 322_HYDRO_4 | bus-322 | to_node | fuel_cost | 0 | bus-322
unit__node__direction | 320_PV_1 | bus-320 | to_node | fuel_cost | 0 | bus-320
unit__node__direction | 314_PV_1 | bus-314 | to_node | fuel_cost | 0 | bus-314
unit__node__direction | 314_PV_2 | bus-314 | to_node | fuel_cost | 0 | bus-314
unit__node__direction | 313_PV_1 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 314_PV_3 | bus-314 | to_node | fuel_cost | 0 | bus-314
unit__node__direction | 314_PV_4 | bus-314 | to_node | fuel_cost | 0 | bus-314
unit__node__direction | 313_PV_2 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 310_PV_1 | bus-310 | to_node | fuel_cost | 0 | bus-310
unit__node__direction | 324_PV_1 | bus-324 | to_node | fuel_cost | 0 | bus-324
unit__node__direction | 312_PV_1 | bus-312 | to_node | fuel_cost | 0 | bus-312
unit__node__direction | 310_PV_2 | bus-310 | to_node | fuel_cost | 0 | bus-310
unit__node__direction | 324_PV_2 | bus-324 | to_node | fuel_cost | 0 | bus-324
unit__node__direction | 324_PV_3 | bus-324 | to_node | fuel_cost | 0 | bus-324
unit__node__direction | 113_PV_1 | bus-113 | to_node | fuel_cost | 0 | bus-113
unit__node__direction | 319_PV_1 | bus-319 | to_node | fuel_cost | 0 | bus-319
unit__node__direction | 215_PV_1 | bus-215 | to_node | fuel_cost | 0 | bus-215
unit__node__direction | 102_PV_1 | bus-102 | to_node | fuel_cost | 0 | bus-102
unit__node__direction | 101_PV_1 | bus-101 | to_node | fuel_cost | 0 | bus-101
unit__node__direction | 102_PV_2 | bus-102 | to_node | fuel_cost | 0 | bus-102
unit__node__direction | 104_PV_1 | bus-104 | to_node | fuel_cost | 0 | bus-104
unit__node__direction | 212_CSP_1 | bus-212 | to_node | fuel_cost | 0 | bus-212
unit__node__direction | 101_PV_2 | bus-101 | to_node | fuel_cost | 0 | bus-101
unit__node__direction | 101_PV_3 | bus-101 | to_node | fuel_cost | 0 | bus-101
unit__node__direction | 101_PV_4 | bus-101 | to_node | fuel_cost | 0 | bus-101
unit__node__direction | 103_PV_1 | bus-103 | to_node | fuel_cost | 0 | bus-103
unit__node__direction | 119_PV_1 | bus-119 | to_node | fuel_cost | 0 | bus-119
unit__node__direction | 308_RTPV_1 | bus-308 | to_node | fuel_cost | 0 | bus-308
unit__node__direction | 313_RTPV_1 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_2 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_3 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_4 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_5 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_6 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_7 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_8 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_9 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_10 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_11 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_RTPV_12 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 320_RTPV_1 | bus-320 | to_node | fuel_cost | 0 | bus-320
unit__node__direction | 320_RTPV_2 | bus-320 | to_node | fuel_cost | 0 | bus-320
unit__node__direction | 320_RTPV_3 | bus-320 | to_node | fuel_cost | 0 | bus-320
unit__node__direction | 313_RTPV_13 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 320_RTPV_4 | bus-320 | to_node | fuel_cost | 0 | bus-320
unit__node__direction | 320_RTPV_5 | bus-320 | to_node | fuel_cost | 0 | bus-320
unit__node__direction | 118_RTPV_1 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 118_RTPV_2 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 118_RTPV_3 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 118_RTPV_4 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 118_RTPV_5 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 118_RTPV_6 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 320_RTPV_6 | bus-320 | to_node | fuel_cost | 0 | bus-320
unit__node__direction | 118_RTPV_7 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 118_RTPV_8 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 118_RTPV_9 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 118_RTPV_10 | bus-118 | to_node | fuel_cost | 0 | bus-118
unit__node__direction | 213_RTPV_1 | bus-213 | to_node | fuel_cost | 0 | bus-213
unit__node__direction | 309_WIND_1 | bus-309 | to_node | fuel_cost | 0 | bus-309
unit__node__direction | 317_WIND_1 | bus-317 | to_node | fuel_cost | 0 | bus-317
unit__node__direction | 303_WIND_1 | bus-303 | to_node | fuel_cost | 0 | bus-303
unit__node__direction | 122_WIND_1 | bus-122 | to_node | fuel_cost | 0 | bus-122
unit__node__direction | 313_STORAGE_1 | bus-313 | to_node | fuel_cost | 0 | bus-313
unit__node__direction | 101_CT_1 | bus-101 | to_node | vom_cost | 0 | bus-101
unit__node__direction | 101_CT_2 | bus-101 | to_node | vom_cost | 0 | bus-101
unit__node__direction | 101_STEAM_3 | bus-101 | to_node | vom_cost | 0 | bus-101
unit__node__direction | 101_STEAM_4 | bus-101 | to_node | vom_cost | 0 | bus-101
unit__node__direction | 102_CT_1 | bus-102 | to_node | vom_cost | 0 | bus-102
unit__node__direction | 102_CT_2 | bus-102 | to_node | vom_cost | 0 | bus-102
unit__node__direction | 102_STEAM_3 | bus-102 | to_node | vom_cost | 0 | bus-102
unit__node__direction | 102_STEAM_4 | bus-102 | to_node | vom_cost | 0 | bus-102
unit__node__direction | 107_CC_1 | bus-107 | to_node | vom_cost | 0 | bus-107
unit__node__direction | 113_CT_1 | bus-113 | to_node | vom_cost | 0 | bus-113
unit__node__direction | 113_CT_2 | bus-113 | to_node | vom_cost | 0 | bus-113
unit__node__direction | 113_CT_3 | bus-113 | to_node | vom_cost | 0 | bus-113
unit__node__direction | 113_CT_4 | bus-113 | to_node | vom_cost | 0 | bus-113
unit__node__direction | 115_STEAM_1 | bus-115 | to_node | vom_cost | 0 | bus-115
unit__node__direction | 115_STEAM_2 | bus-115 | to_node | vom_cost | 0 | bus-115
unit__node__direction | 115_STEAM_3 | bus-115 | to_node | vom_cost | 0 | bus-115
unit__node__direction | 116_STEAM_1 | bus-116 | to_node | vom_cost | 0 | bus-116
unit__node__direction | 118_CC_1 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 123_STEAM_2 | bus-123 | to_node | vom_cost | 0 | bus-123
unit__node__direction | 123_STEAM_3 | bus-123 | to_node | vom_cost | 0 | bus-123
unit__node__direction | 123_CT_1 | bus-123 | to_node | vom_cost | 0 | bus-123
unit__node__direction | 123_CT_4 | bus-123 | to_node | vom_cost | 0 | bus-123
unit__node__direction | 123_CT_5 | bus-123 | to_node | vom_cost | 0 | bus-123
unit__node__direction | 201_CT_1 | bus-201 | to_node | vom_cost | 0 | bus-201
unit__node__direction | 201_CT_2 | bus-201 | to_node | vom_cost | 0 | bus-201
unit__node__direction | 201_STEAM_3 | bus-201 | to_node | vom_cost | 0 | bus-201
unit__node__direction | 202_CT_1 | bus-202 | to_node | vom_cost | 0 | bus-202
unit__node__direction | 202_CT_2 | bus-202 | to_node | vom_cost | 0 | bus-202
unit__node__direction | 202_STEAM_3 | bus-202 | to_node | vom_cost | 0 | bus-202
unit__node__direction | 202_STEAM_4 | bus-202 | to_node | vom_cost | 0 | bus-202
unit__node__direction | 207_CT_1 | bus-207 | to_node | vom_cost | 0 | bus-207
unit__node__direction | 207_CT_2 | bus-207 | to_node | vom_cost | 0 | bus-207
unit__node__direction | 213_CC_3 | bus-213 | to_node | vom_cost | 0 | bus-213
unit__node__direction | 213_CT_1 | bus-213 | to_node | vom_cost | 0 | bus-213
unit__node__direction | 213_CT_2 | bus-213 | to_node | vom_cost | 0 | bus-213
unit__node__direction | 215_CT_4 | bus-215 | to_node | vom_cost | 0 | bus-215
unit__node__direction | 215_CT_5 | bus-215 | to_node | vom_cost | 0 | bus-215
unit__node__direction | 216_STEAM_1 | bus-216 | to_node | vom_cost | 0 | bus-216
unit__node__direction | 218_CC_1 | bus-218 | to_node | vom_cost | 0 | bus-218
unit__node__direction | 221_CC_1 | bus-221 | to_node | vom_cost | 0 | bus-221
unit__node__direction | 223_STEAM_1 | bus-223 | to_node | vom_cost | 0 | bus-223
unit__node__direction | 223_STEAM_2 | bus-223 | to_node | vom_cost | 0 | bus-223
unit__node__direction | 223_STEAM_3 | bus-223 | to_node | vom_cost | 0 | bus-223
unit__node__direction | 223_CT_4 | bus-223 | to_node | vom_cost | 0 | bus-223
unit__node__direction | 223_CT_5 | bus-223 | to_node | vom_cost | 0 | bus-223
unit__node__direction | 223_CT_6 | bus-223 | to_node | vom_cost | 0 | bus-223
unit__node__direction | 301_CT_1 | bus-301 | to_node | vom_cost | 0 | bus-301
unit__node__direction | 301_CT_2 | bus-301 | to_node | vom_cost | 0 | bus-301
unit__node__direction | 301_CT_3 | bus-301 | to_node | vom_cost | 0 | bus-301
unit__node__direction | 301_CT_4 | bus-301 | to_node | vom_cost | 0 | bus-301
unit__node__direction | 302_CT_1 | bus-302 | to_node | vom_cost | 0 | bus-302
unit__node__direction | 302_CT_2 | bus-302 | to_node | vom_cost | 0 | bus-302
unit__node__direction | 302_CT_3 | bus-302 | to_node | vom_cost | 0 | bus-302
unit__node__direction | 302_CT_4 | bus-302 | to_node | vom_cost | 0 | bus-302
unit__node__direction | 307_CT_1 | bus-307 | to_node | vom_cost | 0 | bus-307
unit__node__direction | 307_CT_2 | bus-307 | to_node | vom_cost | 0 | bus-307
unit__node__direction | 313_CC_1 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 315_STEAM_1 | bus-315 | to_node | vom_cost | 0 | bus-315
unit__node__direction | 315_STEAM_2 | bus-315 | to_node | vom_cost | 0 | bus-315
unit__node__direction | 315_STEAM_3 | bus-315 | to_node | vom_cost | 0 | bus-315
unit__node__direction | 315_STEAM_4 | bus-315 | to_node | vom_cost | 0 | bus-315
unit__node__direction | 315_STEAM_5 | bus-315 | to_node | vom_cost | 0 | bus-315
unit__node__direction | 315_CT_6 | bus-315 | to_node | vom_cost | 0 | bus-315
unit__node__direction | 315_CT_7 | bus-315 | to_node | vom_cost | 0 | bus-315
unit__node__direction | 315_CT_8 | bus-315 | to_node | vom_cost | 0 | bus-315
unit__node__direction | 316_STEAM_1 | bus-316 | to_node | vom_cost | 0 | bus-316
unit__node__direction | 318_CC_1 | bus-318 | to_node | vom_cost | 0 | bus-318
unit__node__direction | 321_CC_1 | bus-321 | to_node | vom_cost | 0 | bus-321
unit__node__direction | 322_CT_5 | bus-322 | to_node | vom_cost | 0 | bus-322
unit__node__direction | 322_CT_6 | bus-322 | to_node | vom_cost | 0 | bus-322
unit__node__direction | 323_CC_1 | bus-323 | to_node | vom_cost | 0 | bus-323
unit__node__direction | 323_CC_2 | bus-323 | to_node | vom_cost | 0 | bus-323
unit__node__direction | 114_SYNC_COND_1 | bus-114 | to_node | vom_cost | 0 | bus-114
unit__node__direction | 121_NUCLEAR_1 | bus-121 | to_node | vom_cost | 0 | bus-121
unit__node__direction | 122_HYDRO_1 | bus-122 | to_node | vom_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_2 | bus-122 | to_node | vom_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_3 | bus-122 | to_node | vom_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_4 | bus-122 | to_node | vom_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_5 | bus-122 | to_node | vom_cost | 0 | bus-122
unit__node__direction | 122_HYDRO_6 | bus-122 | to_node | vom_cost | 0 | bus-122
unit__node__direction | 201_HYDRO_4 | bus-201 | to_node | vom_cost | 0 | bus-201
unit__node__direction | 214_SYNC_COND_1 | bus-214 | to_node | vom_cost | 0 | bus-214
unit__node__direction | 215_HYDRO_1 | bus-215 | to_node | vom_cost | 0 | bus-215
unit__node__direction | 215_HYDRO_2 | bus-215 | to_node | vom_cost | 0 | bus-215
unit__node__direction | 215_HYDRO_3 | bus-215 | to_node | vom_cost | 0 | bus-215
unit__node__direction | 222_HYDRO_1 | bus-222 | to_node | vom_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_2 | bus-222 | to_node | vom_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_3 | bus-222 | to_node | vom_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_4 | bus-222 | to_node | vom_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_5 | bus-222 | to_node | vom_cost | 0 | bus-222
unit__node__direction | 222_HYDRO_6 | bus-222 | to_node | vom_cost | 0 | bus-222
unit__node__direction | 314_SYNC_COND_1 | bus-314 | to_node | vom_cost | 0 | bus-314
unit__node__direction | 322_HYDRO_1 | bus-322 | to_node | vom_cost | 0 | bus-322
unit__node__direction | 322_HYDRO_2 | bus-322 | to_node | vom_cost | 0 | bus-322
unit__node__direction | 322_HYDRO_3 | bus-322 | to_node | vom_cost | 0 | bus-322
unit__node__direction | 322_HYDRO_4 | bus-322 | to_node | vom_cost | 0 | bus-322
unit__node__direction | 320_PV_1 | bus-320 | to_node | vom_cost | 0 | bus-320
unit__node__direction | 314_PV_1 | bus-314 | to_node | vom_cost | 0 | bus-314
unit__node__direction | 314_PV_2 | bus-314 | to_node | vom_cost | 0 | bus-314
unit__node__direction | 313_PV_1 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 314_PV_3 | bus-314 | to_node | vom_cost | 0 | bus-314
unit__node__direction | 314_PV_4 | bus-314 | to_node | vom_cost | 0 | bus-314
unit__node__direction | 313_PV_2 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 310_PV_1 | bus-310 | to_node | vom_cost | 0 | bus-310
unit__node__direction | 324_PV_1 | bus-324 | to_node | vom_cost | 0 | bus-324
unit__node__direction | 312_PV_1 | bus-312 | to_node | vom_cost | 0 | bus-312
unit__node__direction | 310_PV_2 | bus-310 | to_node | vom_cost | 0 | bus-310
unit__node__direction | 324_PV_2 | bus-324 | to_node | vom_cost | 0 | bus-324
unit__node__direction | 324_PV_3 | bus-324 | to_node | vom_cost | 0 | bus-324
unit__node__direction | 113_PV_1 | bus-113 | to_node | vom_cost | 0 | bus-113
unit__node__direction | 319_PV_1 | bus-319 | to_node | vom_cost | 0 | bus-319
unit__node__direction | 215_PV_1 | bus-215 | to_node | vom_cost | 0 | bus-215
unit__node__direction | 102_PV_1 | bus-102 | to_node | vom_cost | 0 | bus-102
unit__node__direction | 101_PV_1 | bus-101 | to_node | vom_cost | 0 | bus-101
unit__node__direction | 102_PV_2 | bus-102 | to_node | vom_cost | 0 | bus-102
unit__node__direction | 104_PV_1 | bus-104 | to_node | vom_cost | 0 | bus-104
unit__node__direction | 212_CSP_1 | bus-212 | to_node | vom_cost | 1100 | bus-212
unit__node__direction | 101_PV_2 | bus-101 | to_node | vom_cost | 0 | bus-101
unit__node__direction | 101_PV_3 | bus-101 | to_node | vom_cost | 0 | bus-101
unit__node__direction | 101_PV_4 | bus-101 | to_node | vom_cost | 0 | bus-101
unit__node__direction | 103_PV_1 | bus-103 | to_node | vom_cost | 0 | bus-103
unit__node__direction | 119_PV_1 | bus-119 | to_node | vom_cost | 0 | bus-119
unit__node__direction | 308_RTPV_1 | bus-308 | to_node | vom_cost | 0 | bus-308
unit__node__direction | 313_RTPV_1 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_2 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_3 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_4 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_5 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_6 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_7 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_8 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_9 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_10 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_11 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 313_RTPV_12 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 320_RTPV_1 | bus-320 | to_node | vom_cost | 0 | bus-320
unit__node__direction | 320_RTPV_2 | bus-320 | to_node | vom_cost | 0 | bus-320
unit__node__direction | 320_RTPV_3 | bus-320 | to_node | vom_cost | 0 | bus-320
unit__node__direction | 313_RTPV_13 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 320_RTPV_4 | bus-320 | to_node | vom_cost | 0 | bus-320
unit__node__direction | 320_RTPV_5 | bus-320 | to_node | vom_cost | 0 | bus-320
unit__node__direction | 118_RTPV_1 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 118_RTPV_2 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 118_RTPV_3 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 118_RTPV_4 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 118_RTPV_5 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 118_RTPV_6 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 320_RTPV_6 | bus-320 | to_node | vom_cost | 0 | bus-320
unit__node__direction | 118_RTPV_7 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 118_RTPV_8 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 118_RTPV_9 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 118_RTPV_10 | bus-118 | to_node | vom_cost | 0 | bus-118
unit__node__direction | 213_RTPV_1 | bus-213 | to_node | vom_cost | 0 | bus-213
unit__node__direction | 309_WIND_1 | bus-309 | to_node | vom_cost | 0 | bus-309
unit__node__direction | 317_WIND_1 | bus-317 | to_node | vom_cost | 0 | bus-317
unit__node__direction | 303_WIND_1 | bus-303 | to_node | vom_cost | 0 | bus-303
unit__node__direction | 122_WIND_1 | bus-122 | to_node | vom_cost | 0 | bus-122
unit__node__direction | 313_STORAGE_1 | bus-313 | to_node | vom_cost | 0 | bus-313
unit__node__direction | 101_CT_1 | bus-101 | to_node | minimum_operating_point | 0.4 | bus-101
unit__node__direction | 101_CT_2 | bus-101 | to_node | minimum_operating_point | 0.4 | bus-101
unit__node__direction | 101_STEAM_3 | bus-101 | to_node | minimum_operating_point | 0.39474 | bus-101
unit__node__direction | 101_STEAM_4 | bus-101 | to_node | minimum_operating_point | 0.39474 | bus-101
unit__node__direction | 102_CT_1 | bus-102 | to_node | minimum_operating_point | 0.4 | bus-102
unit__node__direction | 102_CT_2 | bus-102 | to_node | minimum_operating_point | 0.4 | bus-102
unit__node__direction | 102_STEAM_3 | bus-102 | to_node | minimum_operating_point | 0.39474 | bus-102
unit__node__direction | 102_STEAM_4 | bus-102 | to_node | minimum_operating_point | 0.39474 | bus-102
unit__node__direction | 107_CC_1 | bus-107 | to_node | minimum_operating_point | 0.47887 | bus-107
unit__node__direction | 113_CT_1 | bus-113 | to_node | minimum_operating_point | 0.4 | bus-113
unit__node__direction | 113_CT_2 | bus-113 | to_node | minimum_operating_point | 0.4 | bus-113
unit__node__direction | 113_CT_3 | bus-113 | to_node | minimum_operating_point | 0.4 | bus-113
unit__node__direction | 113_CT_4 | bus-113 | to_node | minimum_operating_point | 0.4 | bus-113
unit__node__direction | 115_STEAM_1 | bus-115 | to_node | minimum_operating_point | 0.41667 | bus-115
unit__node__direction | 115_STEAM_2 | bus-115 | to_node | minimum_operating_point | 0.41667 | bus-115
unit__node__direction | 115_STEAM_3 | bus-115 | to_node | minimum_operating_point | 0.4 | bus-115
unit__node__direction | 116_STEAM_1 | bus-116 | to_node | minimum_operating_point | 0.4 | bus-116
unit__node__direction | 118_CC_1 | bus-118 | to_node | minimum_operating_point | 0.47887 | bus-118
unit__node__direction | 123_STEAM_2 | bus-123 | to_node | minimum_operating_point | 0.4 | bus-123
unit__node__direction | 123_STEAM_3 | bus-123 | to_node | minimum_operating_point | 0.4 | bus-123
unit__node__direction | 123_CT_1 | bus-123 | to_node | minimum_operating_point | 0.4 | bus-123
unit__node__direction | 123_CT_4 | bus-123 | to_node | minimum_operating_point | 0.4 | bus-123
unit__node__direction | 123_CT_5 | bus-123 | to_node | minimum_operating_point | 0.4 | bus-123
unit__node__direction | 201_CT_1 | bus-201 | to_node | minimum_operating_point | 0.4 | bus-201
unit__node__direction | 201_CT_2 | bus-201 | to_node | minimum_operating_point | 0.4 | bus-201
unit__node__direction | 201_STEAM_3 | bus-201 | to_node | minimum_operating_point | 0.39474 | bus-201
unit__node__direction | 202_CT_1 | bus-202 | to_node | minimum_operating_point | 0.4 | bus-202
unit__node__direction | 202_CT_2 | bus-202 | to_node | minimum_operating_point | 0.4 | bus-202
unit__node__direction | 202_STEAM_3 | bus-202 | to_node | minimum_operating_point | 0.39474 | bus-202
unit__node__direction | 202_STEAM_4 | bus-202 | to_node | minimum_operating_point | 0.39474 | bus-202
unit__node__direction | 207_CT_1 | bus-207 | to_node | minimum_operating_point | 0.4 | bus-207
unit__node__direction | 207_CT_2 | bus-207 | to_node | minimum_operating_point | 0.4 | bus-207
unit__node__direction | 213_CC_3 | bus-213 | to_node | minimum_operating_point | 0.47887 | bus-213
unit__node__direction | 213_CT_1 | bus-213 | to_node | minimum_operating_point | 0.4 | bus-213
unit__node__direction | 213_CT_2 | bus-213 | to_node | minimum_operating_point | 0.4 | bus-213
unit__node__direction | 215_CT_4 | bus-215 | to_node | minimum_operating_point | 0.4 | bus-215
unit__node__direction | 215_CT_5 | bus-215 | to_node | minimum_operating_point | 0.4 | bus-215
unit__node__direction | 216_STEAM_1 | bus-216 | to_node | minimum_operating_point | 0.4 | bus-216
unit__node__direction | 218_CC_1 | bus-218 | to_node | minimum_operating_point | 0.47887 | bus-218
unit__node__direction | 221_CC_1 | bus-221 | to_node | minimum_operating_point | 0.47887 | bus-221
unit__node__direction | 223_STEAM_1 | bus-223 | to_node | minimum_operating_point | 0.4 | bus-223
unit__node__direction | 223_STEAM_2 | bus-223 | to_node | minimum_operating_point | 0.4 | bus-223
unit__node__direction | 223_STEAM_3 | bus-223 | to_node | minimum_operating_point | 0.4 | bus-223
unit__node__direction | 223_CT_4 | bus-223 | to_node | minimum_operating_point | 0.4 | bus-223
unit__node__direction | 223_CT_5 | bus-223 | to_node | minimum_operating_point | 0.4 | bus-223
unit__node__direction | 223_CT_6 | bus-223 | to_node | minimum_operating_point | 0.4 | bus-223
unit__node__direction | 301_CT_1 | bus-301 | to_node | minimum_operating_point | 0.4 | bus-301
unit__node__direction | 301_CT_2 | bus-301 | to_node | minimum_operating_point | 0.4 | bus-301
unit__node__direction | 301_CT_3 | bus-301 | to_node | minimum_operating_point | 0.4 | bus-301
unit__node__direction | 301_CT_4 | bus-301 | to_node | minimum_operating_point | 0.4 | bus-301
unit__node__direction | 302_CT_1 | bus-302 | to_node | minimum_operating_point | 0.4 | bus-302
unit__node__direction | 302_CT_2 | bus-302 | to_node | minimum_operating_point | 0.4 | bus-302
unit__node__direction | 302_CT_3 | bus-302 | to_node | minimum_operating_point | 0.4 | bus-302
unit__node__direction | 302_CT_4 | bus-302 | to_node | minimum_operating_point | 0.4 | bus-302
unit__node__direction | 307_CT_1 | bus-307 | to_node | minimum_operating_point | 0.4 | bus-307
unit__node__direction | 307_CT_2 | bus-307 | to_node | minimum_operating_point | 0.4 | bus-307
unit__node__direction | 313_CC_1 | bus-313 | to_node | minimum_operating_point | 0.47887 | bus-313
unit__node__direction | 315_STEAM_1 | bus-315 | to_node | minimum_operating_point | 0.41667 | bus-315
unit__node__direction | 315_STEAM_2 | bus-315 | to_node | minimum_operating_point | 0.41667 | bus-315
unit__node__direction | 315_STEAM_3 | bus-315 | to_node | minimum_operating_point | 0.41667 | bus-315
unit__node__direction | 315_STEAM_4 | bus-315 | to_node | minimum_operating_point | 0.41667 | bus-315
unit__node__direction | 315_STEAM_5 | bus-315 | to_node | minimum_operating_point | 0.41667 | bus-315
unit__node__direction | 315_CT_6 | bus-315 | to_node | minimum_operating_point | 0.4 | bus-315
unit__node__direction | 315_CT_7 | bus-315 | to_node | minimum_operating_point | 0.4 | bus-315
unit__node__direction | 315_CT_8 | bus-315 | to_node | minimum_operating_point | 0.4 | bus-315
unit__node__direction | 316_STEAM_1 | bus-316 | to_node | minimum_operating_point | 0.4 | bus-316
unit__node__direction | 318_CC_1 | bus-318 | to_node | minimum_operating_point | 0.47887 | bus-318
unit__node__direction | 321_CC_1 | bus-321 | to_node | minimum_operating_point | 0.47887 | bus-321
unit__node__direction | 322_CT_5 | bus-322 | to_node | minimum_operating_point | 0.4 | bus-322
unit__node__direction | 322_CT_6 | bus-322 | to_node | minimum_operating_point | 0.4 | bus-322
unit__node__direction | 323_CC_1 | bus-323 | to_node | minimum_operating_point | 0.47887 | bus-323
unit__node__direction | 323_CC_2 | bus-323 | to_node | minimum_operating_point | 0.47887 | bus-323
unit__node__direction | 114_SYNC_COND_1 | bus-114 | to_node | minimum_operating_point | 0 | bus-114
unit__node__direction | 121_NUCLEAR_1 | bus-121 | to_node | minimum_operating_point | 0.99 | bus-121
unit__node__direction | 122_HYDRO_1 | bus-122 | to_node | minimum_operating_point | 0 | bus-122
unit__node__direction | 122_HYDRO_2 | bus-122 | to_node | minimum_operating_point | 0 | bus-122
unit__node__direction | 122_HYDRO_3 | bus-122 | to_node | minimum_operating_point | 0 | bus-122
unit__node__direction | 122_HYDRO_4 | bus-122 | to_node | minimum_operating_point | 0 | bus-122
unit__node__direction | 122_HYDRO_5 | bus-122 | to_node | minimum_operating_point | 0 | bus-122
unit__node__direction | 122_HYDRO_6 | bus-122 | to_node | minimum_operating_point | 0 | bus-122
unit__node__direction | 201_HYDRO_4 | bus-201 | to_node | minimum_operating_point | 0 | bus-201
unit__node__direction | 214_SYNC_COND_1 | bus-214 | to_node | minimum_operating_point | 0 | bus-214
unit__node__direction | 215_HYDRO_1 | bus-215 | to_node | minimum_operating_point | 0 | bus-215
unit__node__direction | 215_HYDRO_2 | bus-215 | to_node | minimum_operating_point | 0 | bus-215
unit__node__direction | 215_HYDRO_3 | bus-215 | to_node | minimum_operating_point | 0 | bus-215
unit__node__direction | 222_HYDRO_1 | bus-222 | to_node | minimum_operating_point | 0 | bus-222
unit__node__direction | 222_HYDRO_2 | bus-222 | to_node | minimum_operating_point | 0 | bus-222
unit__node__direction | 222_HYDRO_3 | bus-222 | to_node | minimum_operating_point | 0 | bus-222
unit__node__direction | 222_HYDRO_4 | bus-222 | to_node | minimum_operating_point | 0 | bus-222
unit__node__direction | 222_HYDRO_5 | bus-222 | to_node | minimum_operating_point | 0 | bus-222
unit__node__direction | 222_HYDRO_6 | bus-222 | to_node | minimum_operating_point | 0 | bus-222
unit__node__direction | 314_SYNC_COND_1 | bus-314 | to_node | minimum_operating_point | 0 | bus-314
unit__node__direction | 322_HYDRO_1 | bus-322 | to_node | minimum_operating_point | 0 | bus-322
unit__node__direction | 322_HYDRO_2 | bus-322 | to_node | minimum_operating_point | 0 | bus-322
unit__node__direction | 322_HYDRO_3 | bus-322 | to_node | minimum_operating_point | 0 | bus-322
unit__node__direction | 322_HYDRO_4 | bus-322 | to_node | minimum_operating_point | 0 | bus-322
unit__node__direction | 320_PV_1 | bus-320 | to_node | minimum_operating_point | 0 | bus-320
unit__node__direction | 314_PV_1 | bus-314 | to_node | minimum_operating_point | 0 | bus-314
unit__node__direction | 314_PV_2 | bus-314 | to_node | minimum_operating_point | 0 | bus-314
unit__node__direction | 313_PV_1 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 314_PV_3 | bus-314 | to_node | minimum_operating_point | 0 | bus-314
unit__node__direction | 314_PV_4 | bus-314 | to_node | minimum_operating_point | 0 | bus-314
unit__node__direction | 313_PV_2 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 310_PV_1 | bus-310 | to_node | minimum_operating_point | 0 | bus-310
unit__node__direction | 324_PV_1 | bus-324 | to_node | minimum_operating_point | 0 | bus-324
unit__node__direction | 312_PV_1 | bus-312 | to_node | minimum_operating_point | 0 | bus-312
unit__node__direction | 310_PV_2 | bus-310 | to_node | minimum_operating_point | 0 | bus-310
unit__node__direction | 324_PV_2 | bus-324 | to_node | minimum_operating_point | 0 | bus-324
unit__node__direction | 324_PV_3 | bus-324 | to_node | minimum_operating_point | 0 | bus-324
unit__node__direction | 113_PV_1 | bus-113 | to_node | minimum_operating_point | 0 | bus-113
unit__node__direction | 319_PV_1 | bus-319 | to_node | minimum_operating_point | 0 | bus-319
unit__node__direction | 215_PV_1 | bus-215 | to_node | minimum_operating_point | 0 | bus-215
unit__node__direction | 102_PV_1 | bus-102 | to_node | minimum_operating_point | 0 | bus-102
unit__node__direction | 101_PV_1 | bus-101 | to_node | minimum_operating_point | 0 | bus-101
unit__node__direction | 102_PV_2 | bus-102 | to_node | minimum_operating_point | 0 | bus-102
unit__node__direction | 104_PV_1 | bus-104 | to_node | minimum_operating_point | 0 | bus-104
unit__node__direction | 212_CSP_1 | bus-212 | to_node | minimum_operating_point | 0.15 | bus-212
unit__node__direction | 101_PV_2 | bus-101 | to_node | minimum_operating_point | 0 | bus-101
unit__node__direction | 101_PV_3 | bus-101 | to_node | minimum_operating_point | 0 | bus-101
unit__node__direction | 101_PV_4 | bus-101 | to_node | minimum_operating_point | 0 | bus-101
unit__node__direction | 103_PV_1 | bus-103 | to_node | minimum_operating_point | 0 | bus-103
unit__node__direction | 119_PV_1 | bus-119 | to_node | minimum_operating_point | 0 | bus-119
unit__node__direction | 308_RTPV_1 | bus-308 | to_node | minimum_operating_point | 0 | bus-308
unit__node__direction | 313_RTPV_1 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_2 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_3 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_4 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_5 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_6 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_7 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_8 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_9 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_10 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_11 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_RTPV_12 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 320_RTPV_1 | bus-320 | to_node | minimum_operating_point | 0 | bus-320
unit__node__direction | 320_RTPV_2 | bus-320 | to_node | minimum_operating_point | 0 | bus-320
unit__node__direction | 320_RTPV_3 | bus-320 | to_node | minimum_operating_point | 0 | bus-320
unit__node__direction | 313_RTPV_13 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 320_RTPV_4 | bus-320 | to_node | minimum_operating_point | 0 | bus-320
unit__node__direction | 320_RTPV_5 | bus-320 | to_node | minimum_operating_point | 0 | bus-320
unit__node__direction | 118_RTPV_1 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 118_RTPV_2 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 118_RTPV_3 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 118_RTPV_4 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 118_RTPV_5 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 118_RTPV_6 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 320_RTPV_6 | bus-320 | to_node | minimum_operating_point | 0 | bus-320
unit__node__direction | 118_RTPV_7 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 118_RTPV_8 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 118_RTPV_9 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 118_RTPV_10 | bus-118 | to_node | minimum_operating_point | 0 | bus-118
unit__node__direction | 213_RTPV_1 | bus-213 | to_node | minimum_operating_point | 0 | bus-213
unit__node__direction | 309_WIND_1 | bus-309 | to_node | minimum_operating_point | 0 | bus-309
unit__node__direction | 317_WIND_1 | bus-317 | to_node | minimum_operating_point | 0 | bus-317
unit__node__direction | 303_WIND_1 | bus-303 | to_node | minimum_operating_point | 0 | bus-303
unit__node__direction | 122_WIND_1 | bus-122 | to_node | minimum_operating_point | 0 | bus-122
unit__node__direction | 313_STORAGE_1 | bus-313 | to_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 313_STORAGE_1 | bus-313 | from_node | unit_capacity | 50 | bus-313
unit__node__direction | 313_STORAGE_1 | bus-313 | from_node | fuel_cost | 0 | bus-313
unit__node__direction | 313_STORAGE_1 | bus-313 | from_node | vom_cost | 0 | bus-313
unit__node__direction | 313_STORAGE_1 | bus-313 | from_node | minimum_operating_point | 0 | bus-313
unit__node__direction | 212_CSP_1 | RES_gen-212_CSP_1 | from_node
unit__node__direction | 320_PV_1 | RES_gen-320_PV_1 | from_node
unit__node__direction | 314_PV_1 | RES_gen-314_PV_1 | from_node
unit__node__direction | 314_PV_2 | RES_gen-314_PV_2 | from_node
unit__node__direction | 313_PV_1 | RES_gen-313_PV_1 | from_node
unit__node__direction | 314_PV_3 | RES_gen-314_PV_3 | from_node
unit__node__direction | 314_PV_4 | RES_gen-314_PV_4 | from_node
unit__node__direction | 313_PV_2 | RES_gen-313_PV_2 | from_node
unit__node__direction | 310_PV_1 | RES_gen-310_PV_1 | from_node
unit__node__direction | 324_PV_1 | RES_gen-324_PV_1 | from_node
unit__node__direction | 312_PV_1 | RES_gen-312_PV_1 | from_node
unit__node__direction | 310_PV_2 | RES_gen-310_PV_2 | from_node
unit__node__direction | 324_PV_2 | RES_gen-324_PV_2 | from_node
unit__node__direction | 324_PV_3 | RES_gen-324_PV_3 | from_node
unit__node__direction | 113_PV_1 | RES_gen-113_PV_1 | from_node
unit__node__direction | 319_PV_1 | RES_gen-319_PV_1 | from_node
unit__node__direction | 215_PV_1 | RES_gen-215_PV_1 | from_node
unit__node__direction | 102_PV_1 | RES_gen-102_PV_1 | from_node
unit__node__direction | 101_PV_1 | RES_gen-101_PV_1 | from_node
unit__node__direction | 102_PV_2 | RES_gen-102_PV_2 | from_node
unit__node__direction | 104_PV_1 | RES_gen-104_PV_1 | from_node
unit__node__direction | 101_PV_2 | RES_gen-101_PV_2 | from_node
unit__node__direction | 101_PV_3 | RES_gen-101_PV_3 | from_node
unit__node__direction | 101_PV_4 | RES_gen-101_PV_4 | from_node
unit__node__direction | 103_PV_1 | RES_gen-103_PV_1 | from_node
unit__node__direction | 119_PV_1 | RES_gen-119_PV_1 | from_node
unit__node__direction | 308_RTPV_1 | RES_gen-308_RTPV_1 | from_node
unit__node__direction | 313_RTPV_1 | RES_gen-313_RTPV_1 | from_node
unit__node__direction | 313_RTPV_2 | RES_gen-313_RTPV_2 | from_node
unit__node__direction | 313_RTPV_3 | RES_gen-313_RTPV_3 | from_node
unit__node__direction | 313_RTPV_4 | RES_gen-313_RTPV_4 | from_node
unit__node__direction | 313_RTPV_5 | RES_gen-313_RTPV_5 | from_node
unit__node__direction | 313_RTPV_6 | RES_gen-313_RTPV_6 | from_node
unit__node__direction | 313_RTPV_7 | RES_gen-313_RTPV_7 | from_node
unit__node__direction | 313_RTPV_8 | RES_gen-313_RTPV_8 | from_node
unit__node__direction | 313_RTPV_9 | RES_gen-313_RTPV_9 | from_node
unit__node__direction | 313_RTPV_10 | RES_gen-313_RTPV_10 | from_node
unit__node__direction | 313_RTPV_11 | RES_gen-313_RTPV_11 | from_node
unit__node__direction | 313_RTPV_12 | RES_gen-313_RTPV_12 | from_node
unit__node__direction | 320_RTPV_1 | RES_gen-320_RTPV_1 | from_node
unit__node__direction | 320_RTPV_2 | RES_gen-320_RTPV_2 | from_node
unit__node__direction | 320_RTPV_3 | RES_gen-320_RTPV_3 | from_node
unit__node__direction | 313_RTPV_13 | RES_gen-313_RTPV_13 | from_node
unit__node__direction | 320_RTPV_4 | RES_gen-320_RTPV_4 | from_node
unit__node__direction | 320_RTPV_5 | RES_gen-320_RTPV_5 | from_node
unit__node__direction | 118_RTPV_1 | RES_gen-118_RTPV_1 | from_node
unit__node__direction | 118_RTPV_2 | RES_gen-118_RTPV_2 | from_node
unit__node__direction | 118_RTPV_3 | RES_gen-118_RTPV_3 | from_node
unit__node__direction | 118_RTPV_4 | RES_gen-118_RTPV_4 | from_node
unit__node__direction | 118_RTPV_5 | RES_gen-118_RTPV_5 | from_node
unit__node__direction | 118_RTPV_6 | RES_gen-118_RTPV_6 | from_node
unit__node__direction | 320_RTPV_6 | RES_gen-320_RTPV_6 | from_node
unit__node__direction | 118_RTPV_7 | RES_gen-118_RTPV_7 | from_node
unit__node__direction | 118_RTPV_8 | RES_gen-118_RTPV_8 | from_node
unit__node__direction | 118_RTPV_9 | RES_gen-118_RTPV_9 | from_node
unit__node__direction | 118_RTPV_10 | RES_gen-118_RTPV_10 | from_node
unit__node__direction | 213_RTPV_1 | RES_gen-213_RTPV_1 | from_node
unit__node__direction | 309_WIND_1 | RES_gen-309_WIND_1 | from_node
unit__node__direction | 317_WIND_1 | RES_gen-317_WIND_1 | from_node
unit__node__direction | 303_WIND_1 | RES_gen-303_WIND_1 | from_node
unit__node__direction | 122_WIND_1 | RES_gen-122_WIND_1 | from_node
unit__node__direction | 122_HYDRO_1 | RES_gen-122_HYDRO_1 | from_node
unit__node__direction | 122_HYDRO_2 | RES_gen-122_HYDRO_2 | from_node
unit__node__direction | 122_HYDRO_3 | RES_gen-122_HYDRO_3 | from_node
unit__node__direction | 122_HYDRO_4 | RES_gen-122_HYDRO_4 | from_node
unit__node__direction | 122_HYDRO_5 | RES_gen-122_HYDRO_5 | from_node
unit__node__direction | 122_HYDRO_6 | RES_gen-122_HYDRO_6 | from_node
unit__node__direction | 201_HYDRO_4 | RES_gen-201_HYDRO_4 | from_node
unit__node__direction | 215_HYDRO_1 | RES_gen-215_HYDRO_1 | from_node
unit__node__direction | 215_HYDRO_2 | RES_gen-215_HYDRO_2 | from_node
unit__node__direction | 215_HYDRO_3 | RES_gen-215_HYDRO_3 | from_node
unit__node__direction | 222_HYDRO_1 | RES_gen-222_HYDRO_1 | from_node
unit__node__direction | 222_HYDRO_2 | RES_gen-222_HYDRO_2 | from_node
unit__node__direction | 222_HYDRO_3 | RES_gen-222_HYDRO_3 | from_node
unit__node__direction | 222_HYDRO_4 | RES_gen-222_HYDRO_4 | from_node
unit__node__direction | 222_HYDRO_5 | RES_gen-222_HYDRO_5 | from_node
unit__node__direction | 222_HYDRO_6 | RES_gen-222_HYDRO_6 | from_node
unit__node__direction | 322_HYDRO_1 | RES_gen-322_HYDRO_1 | from_node
unit__node__direction | 322_HYDRO_2 | RES_gen-322_HYDRO_2 | from_node
unit__node__direction | 322_HYDRO_3 | RES_gen-322_HYDRO_3 | from_node
unit__node__direction | 322_HYDRO_4 | RES_gen-322_HYDRO_4 | from_node
unit__node__direction | 100_Dummy | Region-1 | to_node
unit__node__direction | 200_Dummy | Region-2 | to_node
unit__node__direction | 300_Dummy | Region-3 | to_node
unit__node__direction | 100_Spill | Region-1 | from_node
unit__node__direction | 200_Spill | Region-2 | from_node
unit__node__direction | 300_Spill | Region-3 | from_node
unit__node__direction | 212_CSP_1_Curtail | RES_gen-212_CSP_1 | from_node

## rel_unit__node__node
rel_class_name | unit | node | node | parameter_name | value
unit__node__node | 212_CSP_1 | Region-2 | RES_gen-212_CSP_1 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 320_PV_1 | Region-3 | RES_gen-320_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 314_PV_1 | Region-3 | RES_gen-314_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 314_PV_2 | Region-3 | RES_gen-314_PV_2 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_PV_1 | Region-3 | RES_gen-313_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 314_PV_3 | Region-3 | RES_gen-314_PV_3 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 314_PV_4 | Region-3 | RES_gen-314_PV_4 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_PV_2 | Region-3 | RES_gen-313_PV_2 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 310_PV_1 | Region-3 | RES_gen-310_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 324_PV_1 | Region-3 | RES_gen-324_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 312_PV_1 | Region-3 | RES_gen-312_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 310_PV_2 | Region-3 | RES_gen-310_PV_2 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 324_PV_2 | Region-3 | RES_gen-324_PV_2 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 324_PV_3 | Region-3 | RES_gen-324_PV_3 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 113_PV_1 | Region-1 | RES_gen-113_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 319_PV_1 | Region-3 | RES_gen-319_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 215_PV_1 | Region-2 | RES_gen-215_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 102_PV_1 | Region-1 | RES_gen-102_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 101_PV_1 | Region-1 | RES_gen-101_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 102_PV_2 | Region-1 | RES_gen-102_PV_2 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 104_PV_1 | Region-1 | RES_gen-104_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 101_PV_2 | Region-1 | RES_gen-101_PV_2 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 101_PV_3 | Region-1 | RES_gen-101_PV_3 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 101_PV_4 | Region-1 | RES_gen-101_PV_4 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 103_PV_1 | Region-1 | RES_gen-103_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 119_PV_1 | Region-1 | RES_gen-119_PV_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 308_RTPV_1 | Region-3 | RES_gen-308_RTPV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_1 | Region-3 | RES_gen-313_RTPV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_2 | Region-3 | RES_gen-313_RTPV_2 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_3 | Region-3 | RES_gen-313_RTPV_3 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_4 | Region-3 | RES_gen-313_RTPV_4 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_5 | Region-3 | RES_gen-313_RTPV_5 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_6 | Region-3 | RES_gen-313_RTPV_6 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_7 | Region-3 | RES_gen-313_RTPV_7 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_8 | Region-3 | RES_gen-313_RTPV_8 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_9 | Region-3 | RES_gen-313_RTPV_9 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_10 | Region-3 | RES_gen-313_RTPV_10 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_11 | Region-3 | RES_gen-313_RTPV_11 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_12 | Region-3 | RES_gen-313_RTPV_12 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 320_RTPV_1 | Region-3 | RES_gen-320_RTPV_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 320_RTPV_2 | Region-3 | RES_gen-320_RTPV_2 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 320_RTPV_3 | Region-3 | RES_gen-320_RTPV_3 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 313_RTPV_13 | Region-3 | RES_gen-313_RTPV_13 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 320_RTPV_4 | Region-3 | RES_gen-320_RTPV_4 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 320_RTPV_5 | Region-3 | RES_gen-320_RTPV_5 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 118_RTPV_1 | Region-1 | RES_gen-118_RTPV_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 118_RTPV_2 | Region-1 | RES_gen-118_RTPV_2 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 118_RTPV_3 | Region-1 | RES_gen-118_RTPV_3 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 118_RTPV_4 | Region-1 | RES_gen-118_RTPV_4 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 118_RTPV_5 | Region-1 | RES_gen-118_RTPV_5 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 118_RTPV_6 | Region-1 | RES_gen-118_RTPV_6 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 320_RTPV_6 | Region-3 | RES_gen-320_RTPV_6 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 118_RTPV_7 | Region-1 | RES_gen-118_RTPV_7 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 118_RTPV_8 | Region-1 | RES_gen-118_RTPV_8 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 118_RTPV_9 | Region-1 | RES_gen-118_RTPV_9 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 118_RTPV_10 | Region-1 | RES_gen-118_RTPV_10 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 213_RTPV_1 | Region-2 | RES_gen-213_RTPV_1 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 309_WIND_1 | Region-3 | RES_gen-309_WIND_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 317_WIND_1 | Region-3 | RES_gen-317_WIND_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 303_WIND_1 | Region-3 | RES_gen-303_WIND_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 122_WIND_1 | Region-1 | RES_gen-122_WIND_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 122_HYDRO_1 | Region-1 | RES_gen-122_HYDRO_1 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 122_HYDRO_2 | Region-1 | RES_gen-122_HYDRO_2 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 122_HYDRO_3 | Region-1 | RES_gen-122_HYDRO_3 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 122_HYDRO_4 | Region-1 | RES_gen-122_HYDRO_4 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 122_HYDRO_5 | Region-1 | RES_gen-122_HYDRO_5 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 122_HYDRO_6 | Region-1 | RES_gen-122_HYDRO_6 | max_ratio_out_in_unit_flow | 1 | Region-1
unit__node__node | 201_HYDRO_4 | Region-2 | RES_gen-201_HYDRO_4 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 215_HYDRO_1 | Region-2 | RES_gen-215_HYDRO_1 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 215_HYDRO_2 | Region-2 | RES_gen-215_HYDRO_2 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 215_HYDRO_3 | Region-2 | RES_gen-215_HYDRO_3 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 222_HYDRO_1 | Region-2 | RES_gen-222_HYDRO_1 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 222_HYDRO_2 | Region-2 | RES_gen-222_HYDRO_2 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 222_HYDRO_3 | Region-2 | RES_gen-222_HYDRO_3 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 222_HYDRO_4 | Region-2 | RES_gen-222_HYDRO_4 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 222_HYDRO_5 | Region-2 | RES_gen-222_HYDRO_5 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 222_HYDRO_6 | Region-2 | RES_gen-222_HYDRO_6 | max_ratio_out_in_unit_flow | 1 | Region-2
unit__node__node | 322_HYDRO_1 | Region-3 | RES_gen-322_HYDRO_1 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 322_HYDRO_2 | Region-3 | RES_gen-322_HYDRO_2 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 322_HYDRO_3 | Region-3 | RES_gen-322_HYDRO_3 | max_ratio_out_in_unit_flow | 1 | Region-3
unit__node__node | 322_HYDRO_4 | Region-3 | RES_gen-322_HYDRO_4 | max_ratio_out_in_unit_flow | 1 | Region-3

## rel_u__n__n-bus_detailed
rel_class_name | unit | node | node | parameter_name | value
unit__node__node | 212_CSP_1 | bus-212 | RES_gen-212_CSP_1 | max_ratio_out_in_unit_flow | 1 | bus-212
unit__node__node | 320_PV_1 | bus-320 | RES_gen-320_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-320
unit__node__node | 314_PV_1 | bus-314 | RES_gen-314_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-314
unit__node__node | 314_PV_2 | bus-314 | RES_gen-314_PV_2 | max_ratio_out_in_unit_flow | 1 | bus-314
unit__node__node | 313_PV_1 | bus-313 | RES_gen-313_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 314_PV_3 | bus-314 | RES_gen-314_PV_3 | max_ratio_out_in_unit_flow | 1 | bus-314
unit__node__node | 314_PV_4 | bus-314 | RES_gen-314_PV_4 | max_ratio_out_in_unit_flow | 1 | bus-314
unit__node__node | 313_PV_2 | bus-313 | RES_gen-313_PV_2 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 310_PV_1 | bus-310 | RES_gen-310_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-310
unit__node__node | 324_PV_1 | bus-324 | RES_gen-324_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-324
unit__node__node | 312_PV_1 | bus-312 | RES_gen-312_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-312
unit__node__node | 310_PV_2 | bus-310 | RES_gen-310_PV_2 | max_ratio_out_in_unit_flow | 1 | bus-310
unit__node__node | 324_PV_2 | bus-324 | RES_gen-324_PV_2 | max_ratio_out_in_unit_flow | 1 | bus-324
unit__node__node | 324_PV_3 | bus-324 | RES_gen-324_PV_3 | max_ratio_out_in_unit_flow | 1 | bus-324
unit__node__node | 113_PV_1 | bus-113 | RES_gen-113_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-113
unit__node__node | 319_PV_1 | bus-319 | RES_gen-319_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-319
unit__node__node | 215_PV_1 | bus-215 | RES_gen-215_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-215
unit__node__node | 102_PV_1 | bus-102 | RES_gen-102_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-102
unit__node__node | 101_PV_1 | bus-101 | RES_gen-101_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-101
unit__node__node | 102_PV_2 | bus-102 | RES_gen-102_PV_2 | max_ratio_out_in_unit_flow | 1 | bus-102
unit__node__node | 104_PV_1 | bus-104 | RES_gen-104_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-104
unit__node__node | 101_PV_2 | bus-101 | RES_gen-101_PV_2 | max_ratio_out_in_unit_flow | 1 | bus-101
unit__node__node | 101_PV_3 | bus-101 | RES_gen-101_PV_3 | max_ratio_out_in_unit_flow | 1 | bus-101
unit__node__node | 101_PV_4 | bus-101 | RES_gen-101_PV_4 | max_ratio_out_in_unit_flow | 1 | bus-101
unit__node__node | 103_PV_1 | bus-103 | RES_gen-103_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-103
unit__node__node | 119_PV_1 | bus-119 | RES_gen-119_PV_1 | max_ratio_out_in_unit_flow | 1 | bus-119
unit__node__node | 308_RTPV_1 | bus-308 | RES_gen-308_RTPV_1 | max_ratio_out_in_unit_flow | 1 | bus-308
unit__node__node | 313_RTPV_1 | bus-313 | RES_gen-313_RTPV_1 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_2 | bus-313 | RES_gen-313_RTPV_2 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_3 | bus-313 | RES_gen-313_RTPV_3 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_4 | bus-313 | RES_gen-313_RTPV_4 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_5 | bus-313 | RES_gen-313_RTPV_5 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_6 | bus-313 | RES_gen-313_RTPV_6 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_7 | bus-313 | RES_gen-313_RTPV_7 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_8 | bus-313 | RES_gen-313_RTPV_8 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_9 | bus-313 | RES_gen-313_RTPV_9 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_10 | bus-313 | RES_gen-313_RTPV_10 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_11 | bus-313 | RES_gen-313_RTPV_11 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 313_RTPV_12 | bus-313 | RES_gen-313_RTPV_12 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 320_RTPV_1 | bus-320 | RES_gen-320_RTPV_1 | max_ratio_out_in_unit_flow | 1 | bus-320
unit__node__node | 320_RTPV_2 | bus-320 | RES_gen-320_RTPV_2 | max_ratio_out_in_unit_flow | 1 | bus-320
unit__node__node | 320_RTPV_3 | bus-320 | RES_gen-320_RTPV_3 | max_ratio_out_in_unit_flow | 1 | bus-320
unit__node__node | 313_RTPV_13 | bus-313 | RES_gen-313_RTPV_13 | max_ratio_out_in_unit_flow | 1 | bus-313
unit__node__node | 320_RTPV_4 | bus-320 | RES_gen-320_RTPV_4 | max_ratio_out_in_unit_flow | 1 | bus-320
unit__node__node | 320_RTPV_5 | bus-320 | RES_gen-320_RTPV_5 | max_ratio_out_in_unit_flow | 1 | bus-320
unit__node__node | 118_RTPV_1 | bus-118 | RES_gen-118_RTPV_1 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 118_RTPV_2 | bus-118 | RES_gen-118_RTPV_2 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 118_RTPV_3 | bus-118 | RES_gen-118_RTPV_3 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 118_RTPV_4 | bus-118 | RES_gen-118_RTPV_4 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 118_RTPV_5 | bus-118 | RES_gen-118_RTPV_5 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 118_RTPV_6 | bus-118 | RES_gen-118_RTPV_6 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 320_RTPV_6 | bus-320 | RES_gen-320_RTPV_6 | max_ratio_out_in_unit_flow | 1 | bus-320
unit__node__node | 118_RTPV_7 | bus-118 | RES_gen-118_RTPV_7 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 118_RTPV_8 | bus-118 | RES_gen-118_RTPV_8 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 118_RTPV_9 | bus-118 | RES_gen-118_RTPV_9 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 118_RTPV_10 | bus-118 | RES_gen-118_RTPV_10 | max_ratio_out_in_unit_flow | 1 | bus-118
unit__node__node | 213_RTPV_1 | bus-213 | RES_gen-213_RTPV_1 | max_ratio_out_in_unit_flow | 1 | bus-213
unit__node__node | 309_WIND_1 | bus-309 | RES_gen-309_WIND_1 | max_ratio_out_in_unit_flow | 1 | bus-309
unit__node__node | 317_WIND_1 | bus-317 | RES_gen-317_WIND_1 | max_ratio_out_in_unit_flow | 1 | bus-317
unit__node__node | 303_WIND_1 | bus-303 | RES_gen-303_WIND_1 | max_ratio_out_in_unit_flow | 1 | bus-303
unit__node__node | 122_WIND_1 | bus-122 | RES_gen-122_WIND_1 | max_ratio_out_in_unit_flow | 1 | bus-122
unit__node__node | 122_HYDRO_1 | bus-122 | RES_gen-122_HYDRO_1 | max_ratio_out_in_unit_flow | 1 | bus-122
unit__node__node | 122_HYDRO_2 | bus-122 | RES_gen-122_HYDRO_2 | max_ratio_out_in_unit_flow | 1 | bus-122
unit__node__node | 122_HYDRO_3 | bus-122 | RES_gen-122_HYDRO_3 | max_ratio_out_in_unit_flow | 1 | bus-122
unit__node__node | 122_HYDRO_4 | bus-122 | RES_gen-122_HYDRO_4 | max_ratio_out_in_unit_flow | 1 | bus-122
unit__node__node | 122_HYDRO_5 | bus-122 | RES_gen-122_HYDRO_5 | max_ratio_out_in_unit_flow | 1 | bus-122
unit__node__node | 122_HYDRO_6 | bus-122 | RES_gen-122_HYDRO_6 | max_ratio_out_in_unit_flow | 1 | bus-122
unit__node__node | 201_HYDRO_4 | bus-201 | RES_gen-201_HYDRO_4 | max_ratio_out_in_unit_flow | 1 | bus-201
unit__node__node | 215_HYDRO_1 | bus-215 | RES_gen-215_HYDRO_1 | max_ratio_out_in_unit_flow | 1 | bus-215
unit__node__node | 215_HYDRO_2 | bus-215 | RES_gen-215_HYDRO_2 | max_ratio_out_in_unit_flow | 1 | bus-215
unit__node__node | 215_HYDRO_3 | bus-215 | RES_gen-215_HYDRO_3 | max_ratio_out_in_unit_flow | 1 | bus-215
unit__node__node | 222_HYDRO_1 | bus-222 | RES_gen-222_HYDRO_1 | max_ratio_out_in_unit_flow | 1 | bus-222
unit__node__node | 222_HYDRO_2 | bus-222 | RES_gen-222_HYDRO_2 | max_ratio_out_in_unit_flow | 1 | bus-222
unit__node__node | 222_HYDRO_3 | bus-222 | RES_gen-222_HYDRO_3 | max_ratio_out_in_unit_flow | 1 | bus-222
unit__node__node | 222_HYDRO_4 | bus-222 | RES_gen-222_HYDRO_4 | max_ratio_out_in_unit_flow | 1 | bus-222
unit__node__node | 222_HYDRO_5 | bus-222 | RES_gen-222_HYDRO_5 | max_ratio_out_in_unit_flow | 1 | bus-222
unit__node__node | 222_HYDRO_6 | bus-222 | RES_gen-222_HYDRO_6 | max_ratio_out_in_unit_flow | 1 | bus-222
unit__node__node | 322_HYDRO_1 | bus-322 | RES_gen-322_HYDRO_1 | max_ratio_out_in_unit_flow | 1 | bus-322
unit__node__node | 322_HYDRO_2 | bus-322 | RES_gen-322_HYDRO_2 | max_ratio_out_in_unit_flow | 1 | bus-322
unit__node__node | 322_HYDRO_3 | bus-322 | RES_gen-322_HYDRO_3 | max_ratio_out_in_unit_flow | 1 | bus-322
unit__node__node | 322_HYDRO_4 | bus-322 | RES_gen-322_HYDRO_4 | max_ratio_out_in_unit_flow | 1 | bus-322

## rel_unit__cmmdty__dir-gen
rel_class_name | unit | commodity | direction
unit__commodity__direction | 212_CSP_1 | electricity | from_node
unit__commodity__direction | 320_PV_1 | electricity | from_node
unit__commodity__direction | 314_PV_1 | electricity | from_node
unit__commodity__direction | 314_PV_2 | electricity | from_node
unit__commodity__direction | 313_PV_1 | electricity | from_node
unit__commodity__direction | 314_PV_3 | electricity | from_node
unit__commodity__direction | 314_PV_4 | electricity | from_node
unit__commodity__direction | 313_PV_2 | electricity | from_node
unit__commodity__direction | 310_PV_1 | electricity | from_node
unit__commodity__direction | 324_PV_1 | electricity | from_node
unit__commodity__direction | 312_PV_1 | electricity | from_node
unit__commodity__direction | 310_PV_2 | electricity | from_node
unit__commodity__direction | 324_PV_2 | electricity | from_node
unit__commodity__direction | 324_PV_3 | electricity | from_node
unit__commodity__direction | 113_PV_1 | electricity | from_node
unit__commodity__direction | 319_PV_1 | electricity | from_node
unit__commodity__direction | 215_PV_1 | electricity | from_node
unit__commodity__direction | 102_PV_1 | electricity | from_node
unit__commodity__direction | 101_PV_1 | electricity | from_node
unit__commodity__direction | 102_PV_2 | electricity | from_node
unit__commodity__direction | 104_PV_1 | electricity | from_node
unit__commodity__direction | 101_PV_2 | electricity | from_node
unit__commodity__direction | 101_PV_3 | electricity | from_node
unit__commodity__direction | 101_PV_4 | electricity | from_node
unit__commodity__direction | 103_PV_1 | electricity | from_node
unit__commodity__direction | 119_PV_1 | electricity | from_node
unit__commodity__direction | 308_RTPV_1 | electricity | from_node
unit__commodity__direction | 313_RTPV_1 | electricity | from_node
unit__commodity__direction | 313_RTPV_2 | electricity | from_node
unit__commodity__direction | 313_RTPV_3 | electricity | from_node
unit__commodity__direction | 313_RTPV_4 | electricity | from_node
unit__commodity__direction | 313_RTPV_5 | electricity | from_node
unit__commodity__direction | 313_RTPV_6 | electricity | from_node
unit__commodity__direction | 313_RTPV_7 | electricity | from_node
unit__commodity__direction | 313_RTPV_8 | electricity | from_node
unit__commodity__direction | 313_RTPV_9 | electricity | from_node
unit__commodity__direction | 313_RTPV_10 | electricity | from_node
unit__commodity__direction | 313_RTPV_11 | electricity | from_node
unit__commodity__direction | 313_RTPV_12 | electricity | from_node
unit__commodity__direction | 320_RTPV_1 | electricity | from_node
unit__commodity__direction | 320_RTPV_2 | electricity | from_node
unit__commodity__direction | 320_RTPV_3 | electricity | from_node
unit__commodity__direction | 313_RTPV_13 | electricity | from_node
unit__commodity__direction | 320_RTPV_4 | electricity | from_node
unit__commodity__direction | 320_RTPV_5 | electricity | from_node
unit__commodity__direction | 118_RTPV_1 | electricity | from_node
unit__commodity__direction | 118_RTPV_2 | electricity | from_node
unit__commodity__direction | 118_RTPV_3 | electricity | from_node
unit__commodity__direction | 118_RTPV_4 | electricity | from_node
unit__commodity__direction | 118_RTPV_5 | electricity | from_node
unit__commodity__direction | 118_RTPV_6 | electricity | from_node
unit__commodity__direction | 320_RTPV_6 | electricity | from_node
unit__commodity__direction | 118_RTPV_7 | electricity | from_node
unit__commodity__direction | 118_RTPV_8 | electricity | from_node
unit__commodity__direction | 118_RTPV_9 | electricity | from_node
unit__commodity__direction | 118_RTPV_10 | electricity | from_node
unit__commodity__direction | 213_RTPV_1 | electricity | from_node
unit__commodity__direction | 309_WIND_1 | electricity | from_node
unit__commodity__direction | 317_WIND_1 | electricity | from_node
unit__commodity__direction | 303_WIND_1 | electricity | from_node
unit__commodity__direction | 122_WIND_1 | electricity | from_node
unit__commodity__direction | 122_HYDRO_1 | electricity | from_node
unit__commodity__direction | 122_HYDRO_2 | electricity | from_node
unit__commodity__direction | 122_HYDRO_3 | electricity | from_node
unit__commodity__direction | 122_HYDRO_4 | electricity | from_node
unit__commodity__direction | 122_HYDRO_5 | electricity | from_node
unit__commodity__direction | 122_HYDRO_6 | electricity | from_node
unit__commodity__direction | 201_HYDRO_4 | electricity | from_node
unit__commodity__direction | 215_HYDRO_1 | electricity | from_node
unit__commodity__direction | 215_HYDRO_2 | electricity | from_node
unit__commodity__direction | 215_HYDRO_3 | electricity | from_node
unit__commodity__direction | 222_HYDRO_1 | electricity | from_node
unit__commodity__direction | 222_HYDRO_2 | electricity | from_node
unit__commodity__direction | 222_HYDRO_3 | electricity | from_node
unit__commodity__direction | 222_HYDRO_4 | electricity | from_node
unit__commodity__direction | 222_HYDRO_5 | electricity | from_node
unit__commodity__direction | 222_HYDRO_6 | electricity | from_node
unit__commodity__direction | 322_HYDRO_1 | electricity | from_node
unit__commodity__direction | 322_HYDRO_2 | electricity | from_node
unit__commodity__direction | 322_HYDRO_3 | electricity | from_node
unit__commodity__direction | 322_HYDRO_4 | electricity | from_node
unit__commodity__direction | 212_CSP_1_Curtail | electricity | from_node